## README
In the event of a discrepancy between the tables in these sheets and respective tables in the content of SCE's 2026-2028 Wildfire Mitigation Plan, the latest version of SCE's 2026-2028 Wildfire Mitigation Plan in PDF format should be interpreted as containing the latest and correct information.

## Table SCE 2-01
Table SCE 2-01: Responsible Persons
WMP Section | Title | Program Owner
1 | Executive Summary | Ray Fugere, Director, Asset & System Intelligence
2 | Responsible Persons | Ray Fugere, Director, Asset and System Intelligence
3 | Overview of Base WMP | Ray Fugere, Director, Asset and System Intelligence
Gary Chen, Director, Safety & Infrastructure Policy
4 | Overview of the Service Territory | Gary Chen, Director, Safety & Infrastructure Policy
5 | Risk Methodology and Assessment | Seema Turner, Director, Enterprise Risk Management & Public Safety
6 | Wildfire Mitigation Strategy | Ray Fugere, Director, Asset and System Intelligence
7 | Public Safety Power Shutoff | Cameron McPherson, Principal Manager, Electric Transmissions Operations
Thomas Brady, Principal Manager, Business Resiliency
8.0-8.4 | Grid Design and System Hardening | Ray Fugere, Director, Asset and System Intelligence
8.5 | Quality Assurance and Quality Control | Melvin Stark, Principal Manager, Compliance and Quality
8.6 | Work Orders | Ray Fugere, Director, Asset and System Intelligence
8.7 | Grid Operations and Procedures | Andrew Swisher, Consulting Engineer, Asset Engineering
8.8 | Workforce Planning | Ray Fugere, Director, Asset and System Intelligence
9 | Vegetation Management and Inspections | Carter Prescott , Director, Vegetation & Land Management
10.0-10.2 | Situational Awareness Targets, Environmental Monitoring Systems | Melanie Jocelyn, Director, Business Resiliency
10.3 | Grid Monitoring Systems | Andrew Swisher, Consulting Engineer, Asset Engineering
10.4-10.6 | Ignition Detection Systems | Melanie Jocelyn, Director, Business Resiliency
Weather Forecasting
Fire Potential Index
11 | Emergency Preparedness, Collaboration, and Community Outreach Awareness | Melanie Jocelyn, Director, Business Resiliency
Valarie Hernandez, Principal Manager, Customer Service
12 | Enterprise Systems | Brian Taft, Principal Manager, Transmission and Distribution Portfolio Management
13 | Lessons Learned | Ray Fugere, Director, Asset and System Intelligence

## Table 3-1
Table 3-1: List of Risks and Risk Drivers to Prioritize
Priority | Risk | Risk Driver | x% of ignitions in HFTD[1] | Topographical and Climatological Risk Factors[2]
1 | Contact from object | Other contact from object | 18.9% | Wind, temperature, water vapor, turbulence kinetic energy[3], humidity, rain, snow
2 | Equipment / facility failure or damage | Transformer | 12.5% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
3 | Equipment / facility failure or damage | Insulator and bushing | 11.9% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
4 | Equipment / facility failure or damage | Conductor | 10.71% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
5 | Contact from object | Animal contact | 7.14% | Animal/aviation contact incidents
Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
6 | Equipment / facility failure or damage | Other | 6.7% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
7 | Vegetation contact | Fall-in (branch failure) | 5.36% | Routine/hazard tree data; tree density/proximity
|  | Fall-in (trunk failure) |  | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
Fall-in (root failure)
Blow-in
Grow-in
8 | Equipment / facility failure or damage | Connector device | 4.32% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
9 | Contact from object | Balloon contact | 3.57% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
10 | Contact from object | Land vehicle contact | 3.42% | Fatal motor vehicle incidents
Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
11 | Equipment / facility failure or damage | Pole | 2.98% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
12 | Vandalism/ theft | Vandalism/ theft | 1.93% | None. This risk driver is tracked by SCE but is not associated with any associated risk factors.
13 | Equipment / facility failure or damage | Fuse | 1.79% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
13 | Unknown | Unknown | 1.79% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
14 | Equipment / facility failure or damage | Capacitor bank | 1.64% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
15 | Equipment / facility failure or damage | Cross arm | 1.19% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
15 | Equipment / facility failure or damage | Switch | 1.19% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
16 | Equipment / facility failure or damage | Lightning arrestor | 0.89% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
16 | Other | All Other | 0.89% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
17 | Wire-to-wire contact | Wire-to-wire contact | 0.74% | Wind
18 | Utility Work / Operation | Utility Work / Operation | 0.45% | None. This risk driver is tracked by SCE but is not associated with any associated risk factors.
19 | Equipment / facility failure or damage | Anchor/guy | 0% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
19 | Equipment / facility failure or damage | Recloser | 0% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
19 | Equipment / facility failure or damage | Sectionalizer | 0% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
19 | Equipment / facility failure or damage | Voltage regulator/booster | 0% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
19 | Contamination | Contamination | 0% | Wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, snow
19 | Dig-in | Dig-in | 0% | None. This risk driver is tracked by SCE but is not associated with any associated risk factors.
-- | Contact from object | Aircraft vehicle contact | N/A | N/A
-- | Contact from object | 3rd party contact | N/A | N/A
-- | Contact from object | Unknown | N/A | N/A
-- | Equipment / facility failure or damage | Cutout | N/A | N/A
-- | Equipment / facility failure or damage | Relay | N/A | N/A
-- | Equipment / facility failure or damage | Splice | N/A | N/A
-- | Equipment / facility failure or damage | Tap | N/A | N/A
-- | Equipment / facility failure or damage | Tie wire | N/A | N/A
-- | Equipment / facility failure or damage | Unknown | N/A | N/A
-- | Protective device operation | Protective device operation | N/A | N/A
-- | Lightning | Lightning | N/A | N/A
[1] Ignition data spans January 2019 to December 2024 and only considers FIPA (Fire Incident Preliminary Analysis) ignitions. N/A values indicate that the risk factor is not a category that we have used historically.
[2] If listed, risk factors use the following climatological risk factors: wind, temperature, water vapor, turbulence kinetic energy, humidity, rain, and snow. The data is processed by aggregating 10 years of hourly data and calculating several statistical measurements for each climatological factor. These values are then set based on location.
[3] Turbulence kinetic energy is a measure of the intensity of wind turbulence.

## Table 3-2
Table 3-2: SCE Self-Identified Performance Metrics Table
Performance Metric | Assumption that underlies the use of the metric | Mitigation Section associated with the Performance Metric (state “WMP” if the metric applies to entire plan)
1. Number of CPUC reportable ignitions in HFRA | Factors outside of SCE's control (e.g., wind, live fuel moisture) have a significant effect on CPUC reportable ignition counts in HFRA. | WMP
2. Number of wire downs in HFRA | Number of wire down incidents in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may pose a wildfire risk. | WMP
3. Number of outages in HFRA | Number of faults in HFRA based on cause. These metrics may help to provide insight on controllable and uncontrollable risks or help plan future activities to focus on a particular type of fault or outage that may pose a wildfire risk. | WMP
4. Number of asset management ignition risk-related work orders (excluding GO95 exceptions) that are past due | This metric will help track past due work order that are related to wildfire risk mitigation and that are largely {excluding GO95 exceptions) within the utility's control for addressing. | 8.6
5. Number of Tree-Caused Circuit Interruptions (TCCIs) in HFRA | Vegetation that comes into contact with energized circuits can cause a circuit interruption (e.g., fault), however there may be cases with vegetation comes into contact with SCE infrastructure and no fault occurs. | 9
6. Number of trees inspected where at least some vegetation was found in a non-compliant condition in HFRA - Routine | Routine Line Clearing activities will identify instances in which vegetation exists in a non-compliant condition | 9
7. Frequency of PSPS events (total) | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. | WMP
8. Scope of PSPS events (total) | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. | WMP
9. Duration of PSPS (total) | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. | WMP
10. Number of customers impacted by PSPS | Metric does not account for the normalization of weather, fuel conditions, etc., year over year. | WMP
11a. % Customer recall of SCE wildfire and preparedness communications - System Wide | Results can be impacted by volume of PSPS events experienced per year, level of marketing and outreach to customers, severity of fire season, and other factors. | 11
11b. % Customer recall of SCE wildfire and preparedness communications - HFRA only | Results can be impacted by volume of PSPS events experienced per year, level of marketing and outreach to customers, severity of fire season, and other factors. | 11

## Table 3-3
Table 3-3: SCE Summary of Projected WMP Expenditure
Year of WMP Cycle | Spend (thousands $USD)
2026 | Projected = $2,079,412
2027 | Projected = $2,193,381
2028 | Projected = $2,017,891

## Table SCE 3-01
Table SCE 3-01: Plan Objectives
Plan Objective | Related Target(s) | Risk Drivers Addressed | Related Performance Metrics
1. Continue programmatic deployment of covered conductor and targeted undergrounding of distribution lines in SCE’s High-Fire Risk Areas (HFRA) to reduce the likelihood that objects will contact powerlines and lead to an ignition, and to reduce the potential frequency and duration of PSPS events. | SH-1, SH-2 | Contact from object, vegetation contact, Equipment / facility failure or damage, wire-to-wire contact | Number of CPUC reportable ignitions in HFRA, Number of wire downs in HFRA, Number of outages in HFRA, Number of Tree-Caused Circuit Interruptions (TCCIs) in HFRA, Frequency of Public Safety Power Shutoff (PSPS) events (total), Scope of PSPS events (total), Duration of PSPS (total)
2. Continue and expand transmission hardening programs such as proactive splice shunting, enhanced design standards, and evaluation of additional approaches to address ignition drivers on the transmission system. | SH-20, Sections 8.2.6.3, 8.2.13.1 | Contact from object, vegetation contact, wire-to-wire contact, equipment/facility failure or damage | Number of CPUC reportable ignitions in HFRA, Number of wire downs in HFRA, Number of outages in HFRA
3. Continue execution of protection programs (e.g., REFCL, Distribution Open Phase Detection (DOPD), EFD, and fast curve settings) to detect fault current and minimize ignition likelihood. | SH-5, SH-17, SH-18, SA-11, SA-14, Sections 8.2.6, 8.7.1 | Equipment/facility failure or damage | Number of CPUC reportable ignitions in HFRA
4. Execute risk-informed inspections of utility assets for the distribution and transmission system that identify, prioritize, and resolve issues that pose potential ignition sources. | IN-1.1, IN-1.2, IN-3, IN-4, IN-5, IN-10, IN-11, IN-12 | Equipment/facility failure or damage, vegetation contact, wire-to-wire contact | Number of CPUC reportable ignitions in HFRA, Number of wire downs in HFRA, Number of outages in HFRA, Number of asset management ignition risk-related work orders (excluding GO95 exceptions) that are past due
5. Execute utility vegetation management programs to maintain clearances around utility lines, reducing the potential for ignitions due to vegetation contact with energized lines. | VM-1, VM-4, VM-7, VM-8, VM-2.1, VM-2.2, VM-13 | Vegetation contact | Number of CPUC reportable ignitions in HFRA, Number of wire downs in HFRA, Number of outages in HFRA, Number of Tree-Caused Circuit Interruptions in HFRA, Number of trees inspected where at least some vegetation was found in a non-compliant condition in HFRA
6. Maintain and enhance SCE’s extensive network of weather stations, HD cameras, and associated meteorological functions to provide situational awareness to SCE and to external parties such as fire suppression agencies. | SA-3, SA-12, SA-13, SA-15, SA-16, SA-17, SA-18, SA-19 | Does not directly reduce wildfire POI, but enables SCE to evaluate short-term conditions for wildfire and outage program risk | Duration of PSPS, Scope of PSPS events, Number of customers impacted by PSPS
7. Provide effective and accurate communications to the public before, during, and after major outages, PSPS events, and emergencies with information and resources needed to mitigate potential safety and economic impacts. | DEP-1, DEP-4, PSPS-2, PSPS-3, Sections 11.4, 11.5 | PSPS impacts | Percentage of customer recall of SCE wildfire and preparedness communications
8. Maintain a comprehensive, all-hazards planning and preparedness program to provide effective emergency response, safely and expeditiously restore service during and after a major event, and communicate effectively with customers, stakeholders, and agency partners. | DEP-2, DEP-5, Section 11.2 | Reduces all wildfire and outage management risk drivers through procedures that standardize operations, such as precise application of PSPS criteria | Frequency of PSPS events, Scope of PSPS events, Duration of PSPS, Number of customers impacted by PSPS

## Table 4-1
Table 4-1: SCE High-Level Service Territory Components [1]
Characteristic | HFTD Tier 2 | HFTD Tier 3 | Non-HFTD | Total
Area served (sq. mi.) | 9608 | 4707 | 37942 | 52256
Number of customers served (accounts) | 284615 | 462909 | 4521285 | 5268809
Overhead transmission lines (circuit miles) | 1988 | 2429 | 8318 | 12735
Overhead distribution lines (circuit miles) | 3820 | 5522 | 28476 | 37818
Underground transmission lines (circuit miles) | 21 | 45 | 306 | 372
Underground distribution lines (circuit miles) | 3029 | 4318 | 24265 | 31612
[1] Data as of 01/29/25

## Table 4-2
Table 4-2: Catastrophic Wildfires
Ignition Date [1] | Fire Name | Official Cause [2] | Fire Size (acres) | No. of Fatalities | No. of Structures Destroyed and Damaged | Financial Loss (US$) [3] | Lesson(s) Learned
2007-10-20 | RANCH | USFS opined that the fire was caused by SCE equipment | >58,000 | 0 | 9 Structures Damaged or Destroyed | Data not available | See Section 4.2 narrative
2008-11-14 | SAYRE | USFS opined that the fire was caused by SCE equipment | 11262 | 0 | 604 Structures Destroyed / 147 Structures Damaged | Data not available | See Section 4.2 narrative
2015-02-06 | ROUND | CAL FIRE opined that the fire was caused by SCE equipment | 7000 | 0 | 43 Structures Destroyed / 5 Structures Damaged | Data not available | See Section 4.2 narrative
2016-08-18 | REY | USFS opined that the fire was caused by SCE equipment | 32606 | 0 | 5 Structures Destroyed | Data not available | See Section 4.2 narrative
2017-12-04 | THOMAS/ KOENIGSTEIN | CAL FIRE & VCFD opined that the fires were caused by SCE equipment | 281893 | 2 | 1,060 Structures Destroyed / 274 Structures Damaged | Data not available | See Section 4.2 narrative
2017-12-05 | CREEK | USFS opined that fire was caused by LADWP equipment | 15619 | 0 | 123 Structures Destroyed / 81 Structures Damaged | Data not available | See Section 4.2 narrative
2017-12-05 | RYE | CAL FIRE opined that the fire was caused by SCE equipment | 6049 | 0 | 6 Structures Destroyed / 3 Structures Damaged | Data not available | See Section 4.2 narrative
2018-11-08 | WOOLSEY | CAL FIRE opined that the fire was caused by SCE equipment and an unidentified communication line | 96949 | 3 | 1,643 Structures Destroyed / 364 Structures Damaged | Data not available | See Section 4.2 narrative
2019-10-10 | SADDLE RIDGE | Los Angeles City Fire Dept opined that the cause of the fire is undetermined | 8799 | 1 | 24 Structures Destroyed / 91 Structures Damaged | Data not available | See Section 4.2 narrative
2020-09-06 | BOBCAT | USFS opined that the fire was caused by SCE equipment | 115997 | 0 | 169 Structures Destroyed / 47 Structures Damaged | Data not available | See Section 4.2 narrative
2020-10-26 | SILVERADO | CAL FIRE and OCFA opined that the fire was caused by SCE and T-Mobile equipment | 12466 | 0 | 5 Structures Destroyed / 11 Structures Damaged | Data not available | See Section 4.2 narrative
2022-09-05 | FAIRVIEW | CAL FIRE opined that the fire was caused by SCE equipment | 28307 | 2 | 36 Structures Destroyed / 8 Structures Damaged | Data not available | See Section 4.2 narrative
2025-01-07 | EATON | No official cause. Under investigation | 14021 | 17 | 9,413 Structures Destroyed / 1,074 Structures Damaged | Data not available | See Section 4.2 narrative
[1] Wildfire history data is derived from various sources including SCE incident reports and related communications, CAL FIRE (https://www.fire.ca.gov/stats-events/), and U.S Forest Service (https://nap.nwcg.gov/NAP/).
[2] Wildfire history data is derived from various sources including SCE incident reports and related communications, CAL FIRE (https://www.fire.ca.gov/stats-events/), and U.S Forest Service (https://nap.nwcg.gov/NAP/).
[3] In some instances, an agency may provide data related to one component of financial loss such as costs associated with suppression efforts; however, SCE is not aware of an authoritative government source that provides all-inclusive data regarding financial loss.

## Table 4-3
Table 4-3: SCE Frequently Deenergized Circuits
[1] Pursuant to the guidance, SCE has only included circuits that experienced three or more deenergizations in a year for the 6 years prior to the submission of this WMP. Such circuits are not included in years in which they only experienced two or fewer deenergizations.
[2] For Date of Outage, SCE provides the de-energization date. For the dates listed, multiple deenergizations may have occurred on the same date.
[3] For Customer Hours of PSPS per Outage per Circuit, SCE calculates by isolation device or segments the difference between restoration time and deenergization time in hours multiplied by the total number of customers impacted, summed for each circuit. PSPS tracking and reporting varied until 2021. As such, SCE was not able to produce comparable values of customer hours of PSPS per outage per circuit for 2019, 2020, or 2021.
[4] SCE lists here measures taken or planned to reduce PSPS impacts. This might not include all wildfire mitigations on a circuit, as some measures are taken or planned to reduce wildfire risk. For example, there may be more covered conductor, REFCL, or other system hardening performed on each circuit than listed in this table.
Entry # | Circuit ID [1] | Name of Circuit | Dates of Outages [2] | Number of Customers Hours of PSPS per Outage [3] | Measures taken, or planned to be taken, to reduce the need for, and impact of, future PSPS of circuit [4] | Estimated Annual Decline in PSPS Events and PSPS Impact on Customers
1 | ED-00108 | ACOSTA | 2020-12-03 | Data not available | Completed: | This section requests electrical corporations to provide projections for future deenergizations and customer impacts. PSPS are a function of future weather conditions and cannot be predicted with a meaningful level of certainty. Between 2023 and 2025, SCE’s service territory saw more extreme fire weather with each subsequent year prompting an annual increase in PSPS. If in future years current trends of extreme weather and fire conditions continue, PSPS events will continue and may increase in frequency and duration as an essential mitigation to protect public safety.
|  |  | 2020-11-27 |  | • Automated 1 existing switch
|  |  | 2020-10-26 |  | • Implemented operational protocol to raise PSPS windspeed thresholds
|  |  | 2019-10-30 |  | • Replaced 7.28 miles of existing overhead wire with new insulated wire
2019-10-28
2019-10-24
2019-10-10
2 | ED-00452 | AMETHYST | 2020-12-08 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Replaced 1.4 miles of existing overhead wire with new insulated wire
|  |  | 2020-11-27 |  | • Installed an additional weather station to improve situational awareness
2020-10-26
3 | ED-00560 | ANGUS | 2021-11-25 | Data not available | Completed:
|  |  | 2021-11-25 |  | • Replaced 5.66 miles of existing overhead wire with new insulated wire
2021-11-25
2021-01-19
4 | ED-01344 | ANTON | 2024-12-10 | 583 | Completed:
|  |  | 2024-12-09 | 1,926 | • Replaced 27.17 miles of existing overhead wire with new insulated wire
|  |  | 2024-11-06 | 3,304 | • Installed an additional weather station
|  |  | 2023-12-09 | 1,328 | • Installed 1 automated switch and implemented additional segmentation
|  |  | 2023-10-30 | 578 | • Implemented operational protocol to raise PSPS windspeed thresholds
|  |  | 2023-10-29 | 395
|  |  | 2021-11-25 | Data not available | Planned Work:
|  |  | 2021-11-25 |  | • Install 1 automated switch and implement additional segmentation
2021-11-25
2021-01-19
2021-01-19
2021-01-19
2021-01-17
2021-01-15
2020-12-23
2020-12-19
2020-12-19
2020-12-07
2020-12-07
2020-12-03
2020-11-26
2020-10-26
2020-10-26
2020-10-16
2020-09-09
2019-11-17
2019-10-30
2019-10-28
2019-10-24
2019-10-10
5 | ED-00705 | ARLENE | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Replaced 9.04 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Updated switching protocols
2020-11-26
6 | ED-00817 | ATENTO | 2020-12-24 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Replaced 38.34 miles of existing overhead wire with new insulated wire
|  |  | 2020-11-27 |  | • Implemented operational protocols to raise PSPS windspeed thresholds
|  |  | 2020-10-26 |  | • Installed 3 automated switches and implement additional segmentation
7 | ED-00971 | BADGER | 2021-11-25 | Data not available | Completed: • Replaced 1.6 miles of existing overhead wire with new insulated wire
2021-11-21
|  |  | 2021-01-19 |  | Planned Work: • Replace 1.45 miles of existing overhead wire with new insulated wire
8 | ED-00990 | BALCOM | 2024-12-10 | 130 | Completed:
|  |  | 2024-11-06 | 12,583
|  |  | 2024-11-06 | 1,201 | • Replaced 13.86 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-23 | Data not available | • Implemented switching protocols to transfer load to a less affected circuit
|  |  | 2020-12-07 |  | • Installed an additional weather station
2020-12-03
2019-10-30
2019-10-28
2019-10-24
2019-10-10
9 | ED-01630 | BIG ROCK | 2021-11-25 | Data not available | Completed:
|  |  | 2021-01-19 |  | • Replaced 10.69 miles of existing overhead wire with new insulated wire
|  |  | 2021-01-15 |  | • Installed 2 automated switches
|  |  | 2021-01-14 |  | • Installed an additional weather station
|  |  | 2020-12-23 |  | • Implemented operational and switching protocols to transfer load to a less affected circuit
2020-12-07
2020-12-07
2020-12-03
2020-12-03
2020-11-27
2020-11-26
2020-10-26
10 | ED-03314 | BIRCHIM | 2024-11-22 | 6,683 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-10-28 | 1,355
|  |  | 2024-10-27 | 115
|  |  | 2024-10-17 | 11,654
|  |  | 2024-08-24 | 21
11 | ED-01745 | BLACKHILLS | 2021-11-24 | Data not available | Completed: • Replaced 0.68 miles of existing overhead wire with new insulated wire
2021-01-19
|  |  | 2021-01-15 |  | Planned Work: • Replace 0.05 miles of existing overhead wire with new insulated wire
12 | ED-01832 | BLUE CUT | 2024-12-09 | 812 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-11-06 | 471
|  |  | 2024-10-18 | 8,600 | Completed:
|  |  | 2020-12-03 | Data not available | • Replaced 40.43 miles of existing overhead wire with new insulated wire
|  |  | 2020-11-27 |  | Planned Work:
|  |  | 2020-10-26 |  | • Replace 10.51 miles of existing overhead wire with new insulated wire
13 | ED-01954 | BOOTLEGGER | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Insulated Wires: Replaced 28.82 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Implemented switching protocol to remove some customers and critical businesses from PSPS
2020-11-27
2020-10-26
2020-09-09
14 | ED-02035 | BOUQUET | 2019-10-30 | Data not available | Completed:
|  |  | 2019-10-24 |  | • Replaced 30.23 miles of existing overhead wire with new insulated wire
|  |  | 2019-10-10 |  | • Added temporary generator to serve approx. 250 customers during a PSPS event with minimal outages
15 | ED-02191 | BRENNAN | 2023-12-09 | 9,991 | Under engineering review for additional covered conductor scope
|  |  | 2023-11-20 | 1,851
|  |  | 2023-10-29 | 5,566
16 | ED-02261 | BROADCAST | 2024-12-18 | 286 | Under engineering review for potential remote grid / PSPS grid hardening measures
|  |  | 2024-12-09 | 736
|  |  | 2024-11-06 | 3,759
|  |  | 2024-10-18 | 493
17 | ED-02577 | CABANA | 2021-11-24 | Data not available | Completed:
|  |  | 2021-01-19 |  | • Replaced 0.6 miles of existing overhead wire with new insulated wire
2021-01-15
18 | ED-02674 | CALGROVE | 2024-12-17 | 125 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-09 | 182
|  |  | 2024-11-06 | 24,087 | Completed:
|  |  | 2021-11-25 | Data not available | • Replaced 5.67 miles of existing overhead wire with new insulated wire
|  |  | 2021-01-19 |  | • Installed 1 automated switch
|  |  | 2021-01-16 |  | • Installed an additional weather station
2021-01-15
19 | ED-02751 | CALSTATE | 2024-12-17 | 219 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-10 | 248
|  |  | 2024-11-06 | 535 | Completed:
|  |  | 2023-12-09 | 221 | • Replaced 3.04 miles of existing overhead wire with new insulated wire
|  |  | 2023-10-30 | 160
|  |  | 2023-10-29 | 219 | Planned Work:
|  |  | 2021-11-25 | Data not available | • Install 1 automated switch
2021-11-21
2021-01-19
2021-01-15
2020-12-23
2020-12-08
2020-12-03
2020-11-27
2020-10-26
2019-10-30
2019-10-30
2019-10-28
2019-10-24
2019-10-20
2019-10-10
20 | ED-02790 | CAMP BALDY | 2020-12-08 | Data not available | Completed:
|  |  | 2020-11-27 |  | • Installed insulated wire
2020-10-26
21 | ED-03099 | CASMALIA | 2019-10-30 | Data not available | Completed:
|  |  | 2019-10-28 |  | • All existing overhead in HFRA was previously switched to the Impala 12kV
2019-10-24
2019-10-10
22 | ED-04632 | CASTRO | 2021-11-25 | Data not available | Completed:
|  |  | 2021-11-21 |  | • Replaced 18.73 miles of existing overhead wire with new insulated wire
|  |  | 2021-01-19 |  | • Installed 2 automated switches
|  |  | 2020-12-24 |  | • Installed an additional weather station
|  |  | 2020-12-07 |  | • Added a new switch to improve segmentation and reduce customer impacts
2020-12-03
2019-10-30
2019-10-28
2019-10-24
2019-10-11
23 | ED-03714 | COBRA | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Replaced 0.24 miles of existing overhead wire with new insulated wire • Automated 2 existing switches
|  |  | 2020-12-03 |  | • Installed an additional weather station
24 | ED-03885 | CONDOR | 2021-01-19 | Data not available | Completed:
2021-01-19
2021-01-19
|  |  | 2020-12-23 |  | • New insulated wire has already been installed on nearly all existing overhead portions of the circuit
|  |  | 2020-12-08 |  | • Replaced an additional 1.7 miles of existing overhead wire with new insulated wire near the
|  |  | 2020-12-07 |  | substation
2020-12-07
2020-12-03
2020-11-27
2020-11-27
2019-10-30
2019-10-24
2019-10-10
25 | ED-04109 | CORSAIR | 2021-11-25 | Data not available | Completed:
2021-11-25
|  |  | 2021-01-19 |  | • Replaced 70.82 miles of existing overhead wire with new insulated wire
26 | ED-04495 | CUDDEBACK | 2020-12-03 | Data not available | Completed:
|  |  | 2020-12-02 |  | • Replaced 7.53 miles of existing overhead wire with new insulated wire
2020-11-16
2019-10-30
2019-10-28
2019-10-24
2019-10-10
27 | ED-04526 | CUTHBERT | 2024-12-09 | 96270 | Under engineering review for PSPS grid hardening measures (covered conductor and undergrounding)
|  |  | 2024-11-06 | 85942
|  |  | 2024-10-18 | 56731 | Completed:
|  |  | 2021-11-25 | Data not available | • Installed 1 automated switch
|  |  | 2021-11-25 |  | • Replaced 2.02 miles of existing overhead wire with new insulated wire
|  |  | 2021-11-21 |  | • Implemented operational protocols to raise PSPS windspeed thresholds, and transfer load to a less affected circuit
2021-01-19
2021-01-15
28 | ED-04596 | DALBA | 2024-12-09 | 13,344 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-11-06 | 13,795
|  |  | 2024-10-18 | 17,428
29 | ED-04706 | DAVENPORT | 2024-12-10 | 20,265 | Completed:
|  |  | 2024-12-10 | 10,431
|  |  | 2024-11-06 | 5,674 | • Replaced 41.72 miles of existing overhead wire with new insulated wire
|  |  | 2021-01-19 | Data not available
2021-01-19
2021-01-15
2021-01-15
2020-12-07
2020-12-07
2020-12-07
2020-12-03
2020-11-27
2020-11-26
2020-10-26
2020-10-26
2019-10-30
2019-10-28
2019-10-24
2019-10-10
30 | ED-04900 | DE MILLE | 2020-12-08 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Replaced 6.0 miles of existing overhead wire with new insulated wire
|  |  | 2020-10-26 |  | • Circuit cutover to Lopez 16kV which has higher PSPS thresholds
31 | ED-05207 | DONLON | 2021-11-25 | Data not available | Planned Work: • Replace 1.27 miles of existing overhead wire with new insulated wire
2021-01-19
|  |  | 2021-01-19 |  | Completed: • Replaced 6.61 miles of existing overhead wire with new insulated wire
32 | ED-05376 | DUKE | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • New insulated wire on most overhead portions of the circuit within HFRA
|  |  | 2020-12-03 |  | • Replaced 0.4 miles of remaining bare overhead wire within HFRA with new insulated wire
|  |  | 2020-12-02 |  | • Installed 2 automated switches
33 | ED-05483 | DYNAMO | 2019-10-19 | Data not available | Planned Work:
|  |  | 2019-10-17 |  | • Replace 14.24 miles of existing overhead wire with new insulated wire.
2019-09-16
34 | ED-05591 | ECHO | 2020-12-18 | Data not available | Completed:
|  |  | 2020-12-08 |  | • Replaced 2.2 miles of existing overhead wire with new insulated wire
2020-10-26
35 | ED-05930 | ENERGY | 2024-12-17 | 1,351 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-10 | 53,572
|  |  | 2024-12-09 | 1,476 | Completed:
|  |  | 2024-11-06 | 51,376 | • Replaced 27.41 miles of existing overhead wire with new insulated wire
|  |  | 2024-11-06 | 1,915
|  |  | 2024-11-04 | 160 | • Installed 3 automated switches and implement additional segmentation
|  |  | 2024-10-19 | 193 | • Added temporary generator to serve approx. 120 customers during a PSPS event with minimal outages
|  |  | 2023-12-09 | 1,609
|  |  | 2023-11-09 | 462
|  |  | 2023-10-30 | 8,397
|  |  | 2023-10-30 | 195
|  |  | 2023-10-29 | 3,011
|  |  | 2023-10-29 | 2,839
|  |  | 2021-11-25 | Data not available
2021-11-24
2021-11-21
2021-10-16
2021-10-15
2021-10-12
2021-01-19
2021-01-18
2021-01-17
2021-01-15
2021-01-14
2020-12-23
2020-12-20
2020-12-19
2020-12-07
2020-12-03
2020-12-02
2020-11-27
2020-11-26
2020-10-26
2020-10-16
2019-11-26
2019-10-30
2019-10-28
2019-10-24
2019-10-10
36 | ED-06065 | ESTABAN | 2020-12-24 | Data not available | Completed:
|  |  | 2020-12-23 |  | • Replaced 13.8 miles of existing overhead wire with new insulated wire
2020-12-07
2020-12-07
2020-12-03
2020-12-03
2019-10-30
2019-10-24
2019-10-24
2019-10-24
2019-10-10
37 | ED-06357 | FERRARA | 2020-12-08 | Data not available | Planned Work:
|  |  | 2020-11-27 |  | • Replaced 15.84 miles of existing overhead wire with new insulated wire
2020-10-26
38 | ED-06432 | FINGAL | 2020-12-24 | Data not available | Completed:
|  |  | 2020-12-08 |  | • Replaced approximately 33.79 miles of existing overhead wire with new insulated wire
2020-12-07
2020-12-03
39 | ED-06452 | FIREBIRD | 2023-12-09 | 9,037 | Completed:
|  |  | 2023-10-30 | 15,563 | • Replaced 17.59 miles of existing overhead wire with new insulated wire
|  |  | 2023-10-30 | 5,912
40 | ED-06888 | GABBERT | 2021-11-25 | Data not available | Completed:
|  |  | 2021-11-25 |  | • Replaced 2.57 miles of existing overhead wire with new insulated wire
2021-11-25
41 | ED-07382 | GNATCATCHER | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • New insulated wire has already been installed on nearly all existing overhead portions of the circuit
|  |  | 2020-12-03 |  | • Replaced an additional 3.53 miles of existing overhead wire with new insulated wire at various locations
2020-11-27
2019-10-30
2019-10-24
2019-10-10
42 | ED-07742 | GUITAR | 2024-12-10 | 4,604 | Completed:
|  |  | 2024-12-10 | 109 | • Replaced 32.46 miles of existing overhead wire with new insulated wire
|  |  | 2024-11-06 | 8,946
|  |  | 2021-11-25 | Data not available
2021-11-22
2021-01-19
2021-01-19
2021-01-15
2020-12-23
2020-12-03
2020-11-27
2020-10-26
2019-10-30
2019-10-28
2019-10-24
2019-10-11
43 | ED-08446 | HILLFIELD | 2020-12-23 | Data not available | Completed: • Replaced 6.41 miles of existing overhead wire with new insulated wire • Automated 3 switches
|  |  | 2020-12-07 |  | • Updated switching protocols
|  |  | 2020-10-26 |  | • Implemented operational protocol for portions of the circuit
44 | ED-08698 | HORNTOAD | 2024-12-09 | 2,165 | Under engineering review for undergrounding Completed: • Install 1 automated switch
|  |  | 2024-11-06 | 2,706
|  |  | 2024-10-18 | 1,200 | Planned Work: • Install 2 automated switches
45 | ED-08795 | HUCKLEBERRY | 2019-10-30 | Data not available | Completed:
|  |  | 2019-10-28 |  | • Replaced 18.27 miles of existing overhead wire with new insulated wire and implement protocols to transfer load to a less affected circuit
2019-10-24
2019-10-10
46 | ED-08880 | ICE HOUSE | 2020-12-08 | Data not available | Completed:
|  |  | 2020-11-27 |  | • Replaced 1.08 miles of existing overhead wire with new insulated wire
2020-10-26
47 | ED-08904 | IMPALA | 2021-11-25 | Data not available | Completed:
|  |  | 2021-11-24 |  | • Replaced 25.8 miles of existing overhead wire with new insulated wire
2021-11-21
2021-01-19
2020-12-08
2020-12-03
2020-11-27
2020-10-26
2020-10-26
48 | ED-10203 | LAUDA | 2024-12-10 | 25 | Completed:
|  |  | 2024-11-06 | 27 | • Replaced 1.75 miles of existing overhead wire with new insulated wire
|  |  | 2024-11-06 | 28
49 | ED-10483 | LIMITED | 2024-12-17 | 639 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-09 | 4,159
|  |  | 2024-11-06 | 3,956
|  |  | 2024-10-18 | 9,229
50 | ED-10485 | LIMONITE | 2024-12-09 | 75 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-11-07 | 25
|  |  | 2024-11-06 | 6
51 | ED-10705 | LOPEZ | 2020-12-08 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Replaced 22.4 miles of existing overhead wire with new insulated wire
|  |  | 2020-10-26 |  | • Installed 1 automated switch
52 | ED-10729 | LOUCKS | 2020-12-07 | Data not available | Completed:
2020-11-26
2020-10-26
2020-09-09
2019-10-30
2019-10-28
2019-10-24
2019-10-10
53 | ED-10934 | MAGUIRE | 2024-12-17 | 15,439 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-09 | 27,128
|  |  | 2024-11-06 | 37,577
54 | ED-11500 | MCKEVETT | 2019-10-30 | Data not available | Completed:
|  |  | 2019-10-28 |  | • Implemented operational protocol to raise PSPS windspeed thresholds
2019-10-24
2019-10-24
2019-10-11
55 | ED-11695 | MERLIN | 2024-12-10 | 22,102 | Planned Work:
|  |  | 2024-12-09 | 10,291 | • Replace 14.12 miles of existing overhead wire with new underground cable
|  |  | 2024-11-06 | 39,153
56 | ED-11760 | METTLER | 2020-12-07 | Data not available | Completed:
2020-12-07
|  |  | 2020-12-03 |  | • Replaced 38.0 miles of existing overhead wire with new insulated wire
2020-12-02
2020-11-16
2019-10-30
2019-10-28
2019-10-24
2019-10-10
57 | ED-12167 | MORA | 2019-11-01 | Data not available | Completed:
|  |  | 2019-10-30 |  | • Replaced 4.72 miles of existing overhead wire with new insulated wire
2019-10-28
2019-10-24
2019-10-10
58 | ED-1354 | MORGANSTEIN | 2023-12-09 | 40,481 | Under engineering review for PSPS grid hardening measures
|  |  | 2023-11-20 | 12,261
|  |  | 2023-10-29 | 10,370 | Completed:
|  |  | 2021-11-25 | Data not available | • Replace 16.16 miles of existing overhead wire with new insulated wire
2021-11-21
2021-01-19
59 | ED-12482 | NAPA | 2020-12-08 | Data not available | Completed:
|  |  | 2020-12-08 |  | • Replaced 17.40 miles of existing overhead wire with new insulated wire
2020-12-03
2020-12-03
60 | ED-12485 | NAPOLEON | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-08 |  | • Replaced 5.8 miles of existing overhead wire with new insulated wire
2020-12-07
2020-12-03
2020-12-02
61 | ED-12700 | NICHOLAS | 2024-12-17 | 1,786 | Under engineering review for undergrounding
|  |  | 2024-12-09 | 3,761
|  |  | 2024-11-06 | 10,322
|  |  | 2024-10-18 | 4,741
|  |  | 2024-09-09 | 2,119
|  |  | 2023-11-20 | 4,028
|  |  | 2023-11-09 | 2,487
|  |  | 2023-10-30 | 2,714
|  |  | 1029/2023 | 9,213
62 | ED-12847 | NORTHPARK | 2024-12-10 | 14,229 | Completed:
|  |  | 2024-12-10 | 125 | • Replaced 18.6 miles of existing overhead wire with new insulated wire
|  |  | 2024-11-06 | 28,757 | • Implemented switching protocols to transfer load to a less affected circuit
|  |  | 2023-12-09 | 100 | • Automated 2 existing sectionalizing devices
|  |  | 2023-10-30 | 4,186
|  |  | 2023-10-30 | 170
|  |  | 2020-12-24 | Data not available
2020-12-23
2020-12-18
2020-12-03
2020-11-27
63 | ED-13791 | PATRICIA | 2020-12-08 | Data not available | Completed: • Replaced 33.91 miles of existing overhead wire with new insulated wire
2020-12-08
2020-12-07
64 | ED-13918 | PENSTOCK | 2024-12-12 | 18 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-10-18 | 30 | Planned Work:
|  |  | 2024-08-17 | 23 | • Install 1 automated switch
65 | ED-13983 | PETIT | 2019-11-01 | Data not available | Planned Work:
|  |  | 2019-10-30 |  | • Replace 1.21 miles of existing overhead wire with new insulated wire
|  |  | 2019-10-28 |  | Completed:
|  |  | 2019-10-24 |  | • Replaced 4.81 miles of existing overhead wire with new insulated wire
66 | ED-14005 | PHEASANT | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Replaced 9.3 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Installed 2 automated switches
67 | ED-14190 | PLATEAU | 2024-12-17 | 1,883 | Under engineering review for undergrounding
|  |  | 2024-12-09 | 8,073
|  |  | 2024-11-06 | 19,752
|  |  | 2024-10-18 | 3,758
|  |  | 2024-09-09 | 853
|  |  | 2021-11-25 | Data not available
2021-11-25
2021-11-25
2021-01-15
68 | ED-14494 | PURCHASE | 2019-10-30 | Data not available | Completed:
|  |  | 2019-10-30 |  | • Replaced 2.26 miles of existing overhead wire with new insulated wire
2019-10-28
69 | ED-14603 | RACER | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Replaced 0.6 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Implemented operational protocols for portions of the circuit
70 | ED-14645 | RAINBOW | 2021-11-25 | Data not available | Completed:
2021-01-19
|  |  | 2021-01-19 |  | • Replaced 15.82 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-24 |  | • Installed 1 automated switch
2020-12-23
2020-12-07
2020-12-07
2020-12-03
2019-11-01
2019-10-30
2019-10-28
2019-10-28
2019-10-24
71 | ED-14758 | RED BOX | 2024-12-18 | 457 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-09 | 1,172
|  |  | 2024-11-06 | 1,436
|  |  | 2024-10-18 | 788
|  |  | 2020-12-08 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Installed an additional weather station
|  |  | 2020-10-26 |  | • Adjusted switching plans and weather station assignments in order to leverage better situational awareness and reduce PSPS use
2020-09-09
2019-10-30
2019-10-28
2019-10-25
72 | ED-15475 | ROWCO | 2024-12-09 | 28,413 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-11-06 | 2,629
|  |  | 2024-10-18 | 37,191
73 | ED-15586 | RUSTIC | 2020-12-03 | Data not available | Under engineering review for PSPS grid hardening measures
|  |  | 2020-11-27 |  | Completed:
|  |  | 2020-10-26 |  | • Replaced 14.36 miles of existing overhead wire with new insulated wire
74 | ED-15618 | SADDLEBACK | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Replaced 3.25 miles of existing bare overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Added new weather station near end of the circuit to improve situational awareness
75 | ED-15737 | SAND CANYON | 2024-12-09 | 5,430 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-11-06 | 3,798
|  |  | 2024-11-06 | 2,534
|  |  | 2024-10-18 | 220
|  |  | 2023-12-09 | 313
|  |  | 2023-10-29 | 667
|  |  | 2023-10-29 | 413
|  |  | 2021-11-24 | Data not available
2021-11-22
2021-10-15
|  |  | 2021-09-30 |  | Completed:
|  |  | 2021-01-19 |  | • Replaced 30.3 miles of existing overhead wire with new insulated wire.
|  |  | 2021-01-19 |  | • Circuit is fully covered with Raised Wind Speed Thresholds
|  |  | 2021-01-18 |  | • Installed 1 automated switch
|  |  | 2021-01-18 |  | • Identified and increased segmentation for underground portions of the circuit. Updated switching protocols to transfer new segments to an adjacent circuit, mitigating impacts to ~1,800 customers.
2021-01-14
2021-01-14
2020-12-23
2020-12-23
2020-12-18
2020-12-07
2020-12-07
2020-12-03
2020-11-26
2020-11-26
2020-11-17
2020-10-26
2020-10-26
2020-09-09
2019-10-30
2019-10-28
2019-10-24
2019-10-10
76 | ED-15945 | SAVORY | 2020-12-08 | Data not available | Planned Work: • Replace 4.49 miles of existing overhead wire with new insulated wire
2020-12-07
2020-12-03
77 | ED-16170 | SESPE | 2019-10-30 | Data not available | Completed: • Replaced 0.62 miles of existing overhead wire with new insulated wire
2019-10-30
2019-10-11
78 | ED-16404 | SHOVEL | 2020-12-07 | Data not available | Completed:
2020-12-07
2020-12-03
2020-12-03
|  |  | 2020-11-26 |  | • Replaced 40.19 miles of existing overhead wire with new insulated wire and implement protocols to transfer load to a less affected circuit
2020-11-26
2020-11-17
2020-10-26
2020-09-09
2019-10-29
2019-10-28
2019-10-26
2019-10-24
2019-10-20
2019-10-10
79 | ED-16973 | STEEL | 2024-12-09 | 954 | Completed:
|  |  | 2024-11-06 | 381
|  |  | 2024-11-06 | 750 | • Updated switching protocols to reassign the boundary point between PSPS Segment 1 and Segment 2
|  |  | 2021-11-25 | Data not available | • Replaced 6.48 miles of existing overhead wire with new insulated wire
2021-11-21
2021-10-15
2021-01-19
2020-12-23
2020-12-07
2020-12-07
2020-12-03
2019-10-30
2019-10-28
2019-10-24
2019-10-10
80 | ED-14732 | STUBBY | 2024-12-09 | 52 | Completed:
|  |  | 2024-12-09 | 51 | • Replaced 27.82 miles of existing overhead wire with new insulated wire
|  |  | 2024-11-06 | 125
81 | ED-17383 | SUTT | 2021-11-24 | Data not available | Completed: • 3 frequently impacted segments are 100% covered conductor with Raised Wind Speed Thresholds. • Identified and added segmentation for overhead portions of circuit. Updated switching protocols to increase potential customer mitigations. Mitigations dependent on which weather station(s) reaches de-energization thresholds during an event. Reviewing installation of additional remote isolation device. • Installed new weather station 12/13/2023 for increased situtional awareness. Planned Work: • Install 1 automated switch
2021-11-21
2021-01-19
2020-12-18
2020-12-08
2020-10-26
82 | ED-17546 | TAHQUITZ | 2024-12-17 | 548 | Under engineering review for PSPS grid hardening measures
|  |  | 2024-12-10 | 4,132
|  |  | 2024-12-09 | 901
|  |  | 2024-11-06 | 4,812 | Completed:
|  |  | 2019-10-30 | Data not available | • Added new weather station near in the Mountain Center area to improve situational awareness
2019-10-28
2019-10-24
2019-10-11
83 | ED-17487 | TAIWAN | 2020-12-03 | Data not available | Planned Work: • Replace 3.54 miles of existing overhead wire with new insulated wire
2020-10-26
2020-10-26
2019-01-01
2019-01-01
|  |  | 2019-01-01 |  | Completed: • Replaced 11.76 miles of existing overhead wire with new insulated wire
84 | ED-17529 | TANAGER | 2020-12-07 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Replaced 28.87 miles of existing overhead wire with new insulated wire
|  |  | 2020-11-27 |  | • Installed 1 new automated switch
2019-10-30
2019-10-24
2019-10-10
85 | ED-17548 | TAPO | 2020-12-07 | Data not available | Completed:
|  |  | 2020-12-03 |  | • Replaced 11.7 miles of existing overhead wire with new insulated wire
|  |  | 2020-11-26 |  | • Implemented operational protocol to raise PSPS windspeed thresholds
2020-10-26
86 | ED-17880 | TIMBER CANYON | 2021-11-25 | Data not available | Planned Work: • Replace 8.04 miles of existing overhead wire with new insulated wire
2021-11-25
|  |  | 2021-01-19 |  | Completed: • Replaced 25.87 miles of existing overhead wire with new insulated wire
87 | ED-18243 | TUBA | 2019-11-25 | Data not available | Completed:
|  |  | 2019-10-30 |  | • Replaced 3.18 miles of existing overhead wire with new insulated wire
|  |  | 2019-10-24 |  | Planned Work: • Replace 4.97 miles of existing overhead wire with new insulated wire
88 | ED-18252 | TUFA | 2020-12-11 | Data not available | Completed:
|  |  | 2020-11-17 |  | • Replaced 9.41 miles of existing overhead wire with new insulated wire
|  |  | 2020-11-06 |  | Planned Work: • Replace 11.88 miles of existing overhead wire with new insulated wire
89 | ED-18370 | TWIN LAKES | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Implemented operational protocol to raise PSPS windspeed thresholds
|  |  | 2020-12-03 |  | • Implemented switching protocols to isolate overhead portions and transfer customers to adjacent circuits
2020-11-27
2020-10-26
90 | ED-01754 | VARGAS | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-08 |  | • Replaced 0.2 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Installed 1 new automated switch
|  |  | 2020-11-27 |  | • Implemented operational protocol to raise PSPS windspeed thresholds
2020-10-26
91 | ED-18650 | VERA CRUZ | 2020-12-23 | Data not available | Completed:
|  |  | 2020-12-07 |  | • Replaced 8.52 miles of existing overhead wire with new insulated wire
|  |  | 2020-12-03 |  | • Implemented switching protocols to update boundary between PSPS segment 1 and segment 2 • Installed an additional weather station • Installed 1 new automated switch
2020-10-26
92 | ED-19850 | ZONE | 2020-12-07 | Data not available | Completed:
2020-12-07
|  |  | 2020-12-07 |  | • Replaced 23.7 miles of existing overhead wire with new insulated wire
2020-12-03
2020-12-03
|  |  | 2020-12-03 |  | • Implemented operational protocols to raise PSPS
|  |  | 2019-10-30 |  | windspeed thresholds near substation
|  |  | 2019-10-28 |  | • Circuit is fully covered with Raised Wind Speed Thresholds. Identified and added segmentation for overhead portions of circuit. Updated switching protocols to transfer portions to an adjacent circuit. Transfers dependent on which weather station(s) reaches de-energization thresholds during an event.
|  |  | 2019-10-24 |  | • Installed an additional weather station
2019-10-10

## Table 5-1
Table 5-1: SCE Risk Modeling Assumptions and Limitations
| Assumption | Justification | Limitation | Applicable Models
Adaptation of Weather History | SCE leverages 2009-2023 weather data generated from its weather research and forecasting (WRF) | SCE uses machine learning algorithms to associate applicable weather variables from the WRF model at the time of fault/ignition events. | SCE’s WRF has a limited spatial granularity of 2KM x 2KM. | POI
These historical weather data may not be reflective of future weather conditions.
| SCE uses historical FWD from SCE’s historical climatology, as well as data from the most recent California Climate Assessment, where applicable. | These weather days represent fire weather conditions in each of SCE’s FCZs. | To increase accuracy and meet the underlying 30m cell size resolution of the fuels data, 2 KM x 2 KM weather data is interpolated spatially using a bilinear interpolation scheme. | Wildfire Consequence
These historical data may not be reflective of future fire weather conditions.
Availability of Suppression Resources | SCE does not account for historical or future fire suppression. | The use of a consistent unsuppressed truncated 8-hour and 24 wildfire simulations. The use of a consistent simulation time allows for readily comparable results across all assets | There is inherent uncertainty in agent-based activities, such as fire suppression resources. The overlapping jurisdiction, availability, and coordination of resourcing decisions as well as the timeliness of those decision-making processes based on the ignition detection time make it challenging to model. SCE also notes that in many cases, fire agencies must respond to multiple concurrent fire events, adding complexity to wildfire suppression decision-making. Calibration of historical fires alone does not reflect these decision-making processes. In lieu of artificially adjusting consequences based on fire suppression, SCE has chosen not to bias these simulations. | Wildfire Consequence
Height of Wind Driving Fire Spread | Fire simulations require wind speed at midflame to compute surface fire spread and at 20ft to compute crown fire characteristics. To convert the initial 10m wind speeds from WRF to 20ft, we use a wind adjustment factor (WAF) from Andrews (2012). | The model is based on the work of Albini and Baughman (1979) and Baughman and Albini (1980), using some assumptions made by Finney (1998). | The sheltered WAF assumes that the wind speed is approximately constant with height below the top of a uniform forest canopy. Sheltered WAF is based on the fraction of crown space occupied by tree crowns. | Wildfire Consequence
General Equipment Failure Rates | SCE bases its equipment failure rates on its predictive models for Equipment/Facility Failure (EFF) subcomponents using 2015-2023+ equipment failure data for its modeled assets. | SCE uses machine learning algorithms to develop predictive models for equipment failure that are validated and tested for accuracy for inclusion in our probabilistic assessment for risk calculations. | SCE uses historical data which may not be an indicator of future equipment failure rates. | POI
General Vegetation Contact Rates | SCE bases its vegetation contact rates on its predictive model for Contact from Foreign Object (CFO) subcomponent using 2015-2023+ CFO outages for vegetation sub drivers. | SCE uses machine learning algorithms to develop predictive models for vegetation contact that are validated and tested for accuracy for inclusion in our probabilistic assessment for risk calculations. | SCE uses historical data which may not be an indicator of future vegetation contact rates. | POI
Height of Electrical Equipment in the Service Territory | SCE uses current asset condition attributes (e.g., age, voltage, manufacturer, height of pole, etc.) as variables utilized in the machine learning algorithms. The height of electrical equipment is governed by the applicable regulations in GO 95. | SCE’s machine learning models use historical environmental, physical, and electrical variables paired with their actual records of failures to derive statistical insights. | Height of equipment is based on pole height of associated asset and may not reflect actual installation height. | POI
Stability of the Atmosphere | Atmospheric instability, as it related to wildfire propagation after initial ignition, is not considered in the model. | The wildfire propagation model is a surface model is not directly coupled with the atmosphere. It assumes that the heat flux generated by the wildfire will not modify local atmospheric conditions and thus create additional fuel moisture dryness (e.g., pre-heating) in any way. | The intent of the model is to capture the fire propagation at the time of the ignition event through an 8-hour simulated burn period. The resulting wildfire is assumed to be fully developed with fire acceleration, flashover, or decay not being considered. | Wildfire Consequence
Vegetation Fuels | SCE uses the Live/Dead Fuel Moisture Data from the FWD selected. These variables include Dead moisture content, (1hr, 10hr, 100hr, 1000hr) herbaceous moisture content, and live woody moisture content. | Dead fuel moisture is calculated using the Nelson model which is widely used among fire agencies nationwide. Live fuel moisture is calculated using a machine learning approach that was in part developed by SCE. | Modeling fuel moisture is affected by the same limitations that are common in numerical modeling. In addition to the biases and other forecast errors associated with parameters needed to calculate fuel moisture such as temperature, atmospheric moisture, soil moisture, evaporation rates, etc., uncertainties within the physical processes of vegetation phenology compound the errors associated with vegetation moisture outputs | Wildfire Consequence
(See Section 8.3.5).
Vegetation Fuels | Fuels are based on the Timber fuel layers, including an additional 19 custom fuel models. | These fuel models were developed through daily validation of fuels with fire behavior data from CalFire and California National Guard FireGuard data. | These fuel models are static and only represent a snapshot in time at a 30m x 30m resolution. Given limitations in the spatial and temporal granularity of this information (e.g., changes in suburban development between the time the data was captured to present day), this data may not accurately represent details in land/vegetation types at the time of the ignition. | Wildfire Consequence
Additional WUI and Non-Forested Land Use are based on customized fuel models representing fire propagation in those locations. (Technosylva, 2020).
Combination of Risk Components/Weighting of Attributes | The natural unit consequences resulting from wildfire simulations are translated into safety, reliability and consequence scores based on guidance from the most recent applicable Risk Informed Decision- Making Framework Proceeding (RDF) | SCE developed its MAVF based on the principles as set forth in the S-MAP settlement. Appendix B provides further discussion and justification for each of the components. | The attributes are based on observable data and may not reflect other qualitative factors such as egress or customer satisfaction; factors which may not lend themselves to this type of framework. They may also not reflect of associated risk tolerance standards as set forth in other Commission and/or Legislative guidance (e.g., SB 901). | Wildfire Consequence
SCE is an active participant in the CPUC’s RDF.
Wind Load Capacity for Electrical Equipment | SCE assumes the wind load capacity for its electrical equipment is, at minimum, aligned with applicable GO 95 requirements. | SCE is required to maintain the system based on applicable CPUC operating practices. | Equipment failure can occur in both high wind and low/no wind conditions and can be the result of difficult to predict factors, such as animal and vehicles contact. | POI
Number, extent, and type of community assets at risk | Not Applicable | Communities at Risk are not spatially granular enough to adequately represent wildfire risk. For example, the City of Los Angeles is considered a Community at Risk (CAR), though the vast majority of the city is not exposed to wildland fires. | Not Applicable, see comment at left. | Wildfire Consequence
Please also see Section 5.4.
Proxies for estimating impact on customers and communities | SCE assumes only direct impacts to customers. | SCE uses a ratio of 256 structures impacted to one fatality, and a ratio of 107 structures impacted to one serious injury to determine its safety impact. | These estimates are based on recent historical fire information in Southern California and only include reported data. They do not include any potential indirect or unreported impacts. | Wildfire Consequence
Extent, distribution, and characteristics of vulnerable populations | SCE utilizes an AFN/NRCI multiplier on the safety attribute of MAVF. | The AFN/NRCI multiplier is a relative ranking of vulnerability by populations served on individual circuits. | AFN/NRCI weights each population set (AFN customers/NRCI customers) equally and does not differentiate between customer class. Additionally, SCE does not account for customer self-generation capabilities. | Wildfire Consequence

## Table 5-2
Table 5-2: SCE Summary of Design Basis Scenarios
Scenario ID | Design Scenarios | Purpose
(Components)
WL1 | Wind Loading Condition 1 | For Wind and Weather loading conditions, see discussion of FWD selection process in previous sections.
WL2 | Wind Loading Condition 2
WC2 | Weather Condition 2
VC1 | Vegetation Condition 1
VC3 | Vegetation Condition 3

## Table 5-3
Table 5-3: SCE Summary of Extreme-Event Scenarios
Scenario ID | Extreme-Event Scenario | Purpose
ES1: FireSight 8 (Climate) | Climate Change 2050 (Wind) | Determine how the patterns of utility ignition risk may change in the future using CPUC guidance, while leveraging existing wildfire simulation architecture.
Climate Change 2050 (Weather)
Vegetation Condition 3

## Table 5-4
Table 5-4: SCE Summary of Risk Models
ID | Risk Component | Design Scenario(s) | Key Inputs | Source of Inputs (Data and/or Models) | Key Outputs | Units
R1 | Overall utility risk | WL1, WL2, WL3, WL4, | Wildfire risk | See related models | Risk at a specific location, as granular as possible (i.e. circuit segment, pole) | Risk at individual assets
|  | WC2 | Reliability risk
VC3
R2 | Wildfire risk | WL1, WL2, WL3, WL4, WC2 | Ignition likelihood | See related models | Wildfire risk at a specific location | Risk at individual assets
|  | VC3 | Ignition consequence
R3 | Outage program risk | WL1, WL2, WL3, WL4, WC2 | PSPS risk | See related models | Outage program risk at a specific location | Risk at individual assets
|  | VC3 | PEDS risk |  |  | Probability of de-energization (annualized)
IRC1 | Wildfire likelihood | WL1, WL2, WL3, WL4, WC2 | Burn likelihood | See related models | Likelihood of a wildfire occurring given an ignition at a specific location | NA
|  | VC3 | Ignition likelihood |  |  | Probability of ignition (annualized)
IRC2 | Ignition likelihood | WL1, WL2, WL3, WL4, WC2 | Equipment caused likelihood of ignition | See related models | Number of ignitions at a specific location | Probability of ignition (annualized)
|  | VC3 | Contact by vegetation likelihood of ignition Contact by object likelihood of ignition |  |  | Probability of ignition (annualized)
Probability of ignition (annualized)
IRC3 | Wildfire consequence | WL1, WL2, WL3, WL4, WC2 | Wildfire hazard intensity Wildfire exposure potential | See related models | Adverse effects at a specific location per wildfire | See Section 5.2 for additional information
|  | VC3 | Wildfire vulnerability
IRC4 | PSPS risk | WL1, WL2, WL3, WL4, WC2 | PSPS likelihood | See related models | PSPS risk at a specific location | Risk at individual assets
|  | VC3 | PSPS consequence
IRC5 | PSPS likelihood | WL1, WL2, WL3, WL4 | Wind gust velocity | Weather model | Likelihood of PSPS at a specific location per year | Frequency/year
|  | WC2 | Vegetation moisture
VC3
|  | WL1, WL2, WL3, WL4 | Equipment parameters | Asset database | Likelihood of PSPS at a specific location per year | Frequency/year
|  | WC2 | Presence of mitigation
VC3
|  | WL1, WL2, WL3, WL4 | Current status Operating conditions | Data from inspections, work order history, and real-time monitoring systems | Likelihood of PSPS at a specific location per year | Frequency/year
WC2
VC3
IRC6 | PSPS consequence | NA | PSPS exposure potential | See related models | Adverse effects at a specific location per PSPS | See Section 5.2 for additional information
Vulnerability of community to PSPS
IRC7 | PEDS outage risk | WL1, WL2, WL3, WL4, WC2 | PEDS likelihood | See related models | PEDS outage risk at a specific location | Risk at individual assets
|  | VC3 | PEDS consequence
IRC8 | PEDS outage likelihood | WL1, WL2, WL3, WL4 | Wind gust velocity | Weather model | Likelihood of PEDS outage at a specific location per year | Frequency/year
|  | WC2 | Vegetation moisture
VC3
|  | WL1, WL2, WL3, WL4 | Equipment parameters | Asset database | Likelihood of PEDS outage at a specific location per year | Frequency/year
|  | WC2 | Presence of mitigation
VC3
|  | WL1, WL2, WL3, WL4 | Current status Operating conditions | Data from inspections, work order history, and | Likelihood of PEDS outage at a specific location per year | Frequency/year
|  | WC2 |  | real-time monitoring systems
VC3
IRC9 | PEDS outage consequence | NA | PEDS exposure potential | See related models | Adverse effects at a specific location per PEDS outage | (-)/outage location
Vulnerability of community to PEDS
FRC1 | Equipment caused ignition likelihood | WL1, WL2, WL3, WL4 | Wind gust velocity | Weather model | Likelihood of equipment, including failure, causing an ignition | Ignitions/year
|  | WC2 | Vegetation moisture
VC3
|  | WL1, WL2, WL3, WL4 | Equipment parameters | Asset database | Likelihood of equipment, including failure, causing an ignition | Ignitions/year
|  | WC2 | Presence of mitigation
VC3
|  | WL1, WL2, WL3, WL4 | Current status Operating conditions | Data from inspections, work order history, and | Likelihood of equipment, including failure, causing an ignition | Ignitions/year
|  | WC2 |  | real-time monitoring systems
VC3
FRC2 | Contact from vegetation ignition likelihood | WL1, WL2, WL3, WL4 | Wind gust velocity Vegetation moisture | Weather model | Likelihood of vegetation contact causing an ignition | Ignitions/year
WC2
VC3
|  | WL1, WL2, WL3, WL4 | Vegetation parameters | Vegetation database | Likelihood of vegetation contact causing an ignition | Ignitions/year
WC2
VC3
|  | WL1, WL2, WL3, WL4 | Current status | Data from inspections and vegetation treatment | Likelihood of vegetation contact causing an ignition | Ignitions/year
WC2
VC3
FRC3 | Contact from object ignition likelihood | WL1, WL2, WL3, WL4 | Wind gust velocity | Weather model | Likelihood of non-vegetation object contact causing an ignition | Ignitions/year
|  | WC2 | Vegetation moisture
VC3
|  | WL1, WL2, WL3, WL4 | Historic risk events | Data from previous risk events | Likelihood of non-vegetation object contact causing an ignition | Ignitions/year
WC2
VC3
FRC4 | Burn likelihood | WL1, WL2, WL3, WL4 | Topography | LANDFIRE | Likelihood of a fire reaching a location from a nearby but unknown ignition point | NA – see FWD Section 5.2
WC2
VC3
|  | WL1, WL2, WL3, WL4 | Statistical profile of sustained wind speeds | Weather model | Likelihood of a fire reaching a location from a nearby but unknown ignition point | NA – See FWD Section 5.2
WC2
VC3
|  | WL1, WL2, WL3, WL4 | Vegetation | LANDFIRE, adapted based on LiDAR (light detection and ranging) data | Likelihood of a fire reaching a location from a nearby but unknown ignition point | NA – see FWD Section 5.2
WC2
VC3
FRC5 | Wildfire hazard intensity | WL1, WL2, WL3, WL4 | Topography | LANDFIRE | Intensity of a fire at a specific location | NA – see FWD Section 5.2
WC2
VC3
|  | WL1, WL2, WL3, WL4 | Sustained wind speeds | Weather model | Intensity of a fire at a specific location | NA – see FWD Section 5.2
WC2
VC3
|  | WL1, WL2, WL3, WL4 | Vegetation | LANDFIRE, adapted based on LiDAR data | Intensity of a fire at a specific location | NA – see FWD Section 5.2
WC2
VC3
FRC6 | Wildfire exposure potential | NA | Topography | LANDFIRE | Structures, people, and critical infrastructure at a specific location | CPUC HFTD Map
|  | NA | Land use | Remote sensing | Structures, people, and critical infrastructure at a specific location | Fuel Types
|  | NA | Population information | Census | Structures, people, and critical infrastructure at a specific location | Quantity/Location
FRC7 | Wildfire vulnerability | NA | Vulnerable populations (access and functional needs population [AFN], limited English proficiency [LEP], elderly) | Census and surveys | Structures, people, and critical infrastructure at a specific location | Quantity/Location
|  | NA | Land use | Remote sensing | Structures, people, and critical infrastructure at a specific location | Quantity/Location
|  | NA | Critical infrastructure | Local municipalities | Structures, people, and critical infrastructure at a specific location | Quantity/Location
FRC8 | PSPS exposure potential | NA | Topography | LANDFIRE | Structures, people, and critical infrastructure at a specific location | CPUC HFTD Map
|  | NA | Land use | Remote sensing | Structures, people, and critical infrastructure at a specific location | Fuel Types
|  | NA | Population information | Census | Structures, people, and critical infrastructure at a specific location | Quantity/Location
FRC9 | Vulnerability of community to PSPS | NA | Vulnerable populations (AFN, LEP, elderly) | Census and surveys | Structures, people, and critical infrastructure at a specific location | Quantity/Location
|  | NA | Land use | Remote sensing | Structures, people, and critical infrastructure at a specific location | Quantity/Location
|  | NA | Critical infrastructure | Local municipalities | Structures, people, and critical infrastructure at a specific location | Quantity/Location
FRC10 | PEDS outage exposure potential | NA | Topography | LANDFIRE | Structures, people, and critical infrastructure at a specific location | CPUC HFTD Map
|  | NA | Land use | Remote sensing | Structures, people, and critical infrastructure at a specific location | Fuel Types
|  | NA | Population information | Census | Structures, people, and critical infrastructure at a specific location | Quantity/Location
FRC11 | PEDS outage vulnerability | NA | Vulnerable populations (AFN, LEP, elderly) | Census and surveys | Structures, people, and critical infrastructure at a specific location | Quantity/Location
|  | NA | Land use | Remote sensing | Structures, people, and critical infrastructure at a specific location | Quantity/Location
|  | NA | Critical infrastructure | Local municipalities | Structures, people, and critical infrastructure at a specific location | Quantity/Location

## Table 5-5
Table 5-5: SCE Summary of Top-Risk Circuits
Risk Ranking | Circuit, Segment, or Span ID | Overall Utility Risk Score per HFRA Mile | Wildfire Risk Score per HFRA Mile | Outage Program Risk Score per HFRA Mile | Top Risk Contributors | Total Miles in HFRA | Version of Risk Model Used
1 | TUNGSTEN | 0.96292 | 0.96289 | 3.2628e-05 | EFF Risk, CFO Other Risk | 0.82936 | POI 2024, Firesight 8
2 | PHEASANT | 0.29491 | 0.29491 | 1.9522e-06 | EFF Risk, CFO Other Risk | 10.7983 | POI 2024, Firesight 8
3 | LOUCKS | 0.22597 | 0.22597 | 5.3053e-07 | EFF Risk, CFO Other Risk | 5.8977 | POI 2024, Firesight 8
4 | PASCAL | 0.21017 | 0.21017 | 7.1344e-06 | CFO Other Risk, EFF Risk | 10.7783 | POI 2024, Firesight 8
5 | DAVENPORT | 0.18979 | 0.18979 | 2.7882e-07 | EFF Risk, CFO Other Risk | 67.9595 | POI 2024, Firesight 8
6 | CERRITO | 0.18868 | 0.18868 | 5.2824e-05 | EFF Risk, CFO Other Risk | 1.8563 | POI 2024, Firesight 8
7 | RAYBURN | 0.18688 | 0.18688 | 8.3881e-06 | EFF Risk, CFO Other Risk | 11.3077 | POI 2024, Firesight 8
8 | SHOVEL | 0.1773 | 0.17729 | 8.9042e-07 | CFO Other Risk, EFF Risk | 45.6303 | POI 2024, Firesight 8
9 | PELONA | 0.17628 | 0.17627 | 4.8012e-05 | CFO Other Risk, EFF Risk | 1.6956 | POI 2024, Firesight 8
10 | GUFFY | 0.17512 | 0.17512 | 5.3303e-06 | CFO Other Risk, EFF Risk | 4.4569 | POI 2024, Firesight 8
11 | STORES | 0.16823 | 0.16823 | 4.8754e-06 | EFF Risk, CFO Other Risk | 24.9706 | POI 2024, Firesight 8
12 | PURCHASE | 0.1609 | 0.1609 | 1.1797e-06 | EFF Risk, CFO Other Risk | 3.5073 | POI 2024, Firesight 8
13 | ENERGY | 0.15185 | 0.15185 | 3.2892e-06 | CFO Other Risk, EFF Risk | 29.3051 | POI 2024, Firesight 8
14 | ARIEL | 0.15004 | 0.15004 | 0.00010596 | EFF Risk, CFO Other Risk | 0.32661 | POI 2024, Firesight 8
15 | BODKIN | 0.13442 | 0.13442 | 6.4489e-06 | EFF Risk, CFO Other Risk | 1.7426 | POI 2024, Firesight 8
16 | CASCADE | 0.13233 | 0.13233 | 1.1313e-05 | CFO Other Risk, EFF Risk | 6.829 | POI 2024, Firesight 8
17 | IDA | 0.1251 | 0.1251 | 5.7954e-06 | EFF Risk, CFO Other Risk | 10.7621 | POI 2024, Firesight 8
18 | FINGAL | 0.1228 | 0.1228 | 3.9029e-06 | EFF Risk, CFO Other Risk | 36.9522 | POI 2024, Firesight 8
19 | POPPET FLATS | 0.12032 | 0.12032 | 4.3655e-06 | EFF Risk, CFO Other Risk | 33.3709 | POI 2024, Firesight 8
20 | STONEMAN | 0.11761 | 0.11761 | 6.3264e-06 | EFF Risk, CFO Other Risk | 27.1458 | POI 2024, Firesight 8
21 | PIONEERTOWN | 0.11151 | 0.11151 | 1.6619e-06 | EFF Risk, CFO Other Risk | 60.811 | POI 2024, Firesight 8
22 | PICK [1] | 0.10405 | 0.10405 | 2.3214e-06 | CFO Other Risk, EFF Risk | 43.1465 | POI 2024, Firesight 8
23 | IRVINGTON | 0.10252 | 0.10251 | 3.4e-05 | CFO Other Risk, EFF Risk | 0.2523 | POI 2024, Firesight 8
24 | PICONI | 0.10155 | 0.10155 | 1.0342e-05 | EFF Risk, CFO Other Risk | 19.6691 | POI 2024, Firesight 8
25 | SNOWCREEK | 0.099687 | 0.099686 | 7.4466e-07 | EFF Risk, CFO Other Risk | 1.774 | POI 2024, Firesight 8
26 | NUTMEG | 0.099105 | 0.099105 | 5.0905e-06 | EFF Risk, CFO Other Risk | 7.7731 | POI 2024, Firesight 8
27 | SCHMIDT | 0.094033 | 0.094032 | 4.1443e-06 | EFF Risk, CFO Other Risk | 15.3772 | POI 2024, Firesight 8
28 | SEAWOLF | 0.093574 | 0.093573 | 2.2831e-05 | EFF Risk, CFO Other Risk | 1.0036 | POI 2024, Firesight 8
29 | ARAPAHO | 0.092933 | 0.092933 | 3.7747e-06 | EFF Risk, CFO Other Risk | 15.6319 | POI 2024, Firesight 8
30 | MOAB | 0.08632 | 0.08632 | 2.9046e-06 | EFF Risk, CFO Other Risk | 0.56303 | POI 2024, Firesight 8
31 | LUISENO | 0.086239 | 0.086239 | 6.5018e-09 | CFO Other Risk, EFF Risk | 30.2104 | POI 2024, Firesight 8
32 | BALLOON | 0.085087 | 0.085086 | 1.4299e-05 | EFF Risk, CFO Other Risk | 4.2203 | POI 2024, Firesight 8
33 | BOUQUET | 0.084897 | 0.084897 | 1.5258e-06 | EFF Risk, CFO Other Risk | 24.6971 | POI 2024, Firesight 8
34 | CALSPAR | 0.084187 | 0.084179 | 2.2332e-05 | EFF Risk, CFO Other Risk | 0.32672 | POI 2024, Firesight 8
35 | BIG ROCK | 0.083437 | 0.083435 | 1.1135e-05 | CFO Other Risk, EFF Risk | 14.0869 | POI 2024, Firesight 8
36 | STAR ROCK | 0.082824 | 0.082821 | 2.7286e-05 | EFF Risk, CFO Other Risk | 2.3937 | POI 2024, Firesight 8
37 | KELLER | 0.081615 | 0.081615 | 3.02e-05 | EFF Risk, CFO Other Risk | 1.07 | POI 2024, Firesight 8
38 | CORTESE | 0.080793 | 0.080792 | 4.9984e-06 | EFF Risk, CFO Other Risk | 2.1442 | POI 2024, Firesight 8
39 | BOOTLEGGER | 0.080711 | 0.080711 | 1.2079e-06 | EFF Risk, CFO Other Risk | 79.9241 | POI 2024, Firesight 8
40 | UTE | 0.080521 | 0.080521 | 4.0825e-08 | EFF Risk, CFO Other Risk | 1.0015 | POI 2024, Firesight 8
41 | SOUTHRIDGE | 0.080465 | 0.080465 | 2.1626e-06 | EFF Risk, CFO Other Risk | 0.48032 | POI 2024, Firesight 8
42 | MOCKINGBIRD | 0.079654 | 0.079654 | 4.6856e-06 | EFF Risk, CFO Other Risk | 7.0724 | POI 2024, Firesight 8
43 | CORONITA | 0.079501 | 0.079498 | 8.5516e-05 | EFF Risk, CFO Other Risk | 0.45161 | POI 2024, Firesight 8
44 | ATENTO | 0.07787 | 0.077869 | 8.6457e-06 | EFF Risk, CFO Other Risk | 26.6474 | POI 2024, Firesight 8
45 | PAWNEE | 0.07717 | 0.07717 | 4.3562e-06 | CFO Other Risk, EFF Risk | 54.8137 | POI 2024, Firesight 8
46 | INYO LUMBER | 0.076386 | 0.076382 | 7.8323e-06 | EFF Risk, CFO Other Risk | 3.1719 | POI 2024, Firesight 8
47 | PARADISE | 0.075725 | 0.075724 | 3.6399e-06 | EFF Risk, CFO Other Risk | 14.8249 | POI 2024, Firesight 8
48 | PERRIS | 0.075407 | 0.075406 | 1.6511e-05 | EFF Risk, CFO Other Risk | 3.3614 | POI 2024, Firesight 8
49 | RAMSGATE | 0.075018 | 0.075018 | 2.0709e-05 | EFF Risk, CFO Other Risk | 0.91105 | POI 2024, Firesight 8
[1] This circuit is located in the burn scar area of the Lidia Fire in January 2025.

## Table 5-6
Table 5-6: SCE Risk Assessment Improvement Plan
Key Risk Assessment Area | Proposed Improvement | Type of Improvement | Expected Value Add | Timeframe and Key Milestones
RA-1, risk assessment methodology | Reassess fire spread modeling | Technical and programmatic | Mitigation scoping and potentially develop new mitigations | To be completed in 2025; pending results, any implementation planned 2026-2027
RA-1, risk assessment methodology | Explore the inclusion of additional wildfire impacts | Technical | Represent additional impacts of wildfire events, such as more accurate representation of building consequences | 2026
RA-1, risk assessment methodology | Revise Elevated Wildfire Risk Designation – Informs Proposed HFTD Update submitted to the CPUC | Technical and programmatic | Update HFTD boundary to reflect contemporary data and understanding of elevated wildfire risk | SCE has submitted its proposal to the CPUC and is awaiting a schedule for the proceeding
RA-2, design basis | Develop Forward Looking Climate Change Scenario | Technical | Improve understanding of wildfire risk under future conditions | To be completed in 2025; pending results, any implementation planned 2026-2027
RA-3, risk presentation | Enhance WMP Risk Presentation dashboard | Technical | Automate dashboard calculations on a scheduled basis when new data becomes available. | As needed
RA-4, risk event tracking | Update Risk Events Database | Technical and programmatic | Identify broader trends and potentially allow SCE to propose mitigations to address potential issues before risk events occur | Daily

## Table SCE 5-01
Table SCE 5-01: Risk Quantification Factors
Factors | MARS Framework [1] | IWMS Risk Framework [2]
Equipment/Assets | Included in Wildfire POI component | Evaluated during the Review & Revise stage of the IWMS Risk Framework
Topography | Included in Wildfire Consequence Component | Included in Wildfire Consequence Component and in IWMS Risk Framework[3]
Weather | Included in POI and Wildfire Consequence Components | Included in Wildfire Consequence Component and in IWMS Risk Framework
Vegetation | Included in POI and Wildfire Consequence Components | Included in Wildfire Consequence Component and in IWMS Risk Framework
Climate change | Not currently factored [4] | Not currently factored
Social vulnerability | Included in Wildfire and PSPS Consequence Components | Not directly factored
Physical vulnerability | Included in Wildfire and PSPS Consequence Components | Included in IWMS Risk Framework
Access Capacities | Not directly factored | Included in IWMS Risk Framework
[1] The MARS Framework was initially described in Section 5.1.1 and is further described in Section 5.2.1.1.
[2] The IWMS Risk Framework was initially described in Section 5.1.1 and is further described in Section 5.2.1.2.
[3] See Section 5.2.1 for additional details.
[4] See Section 3.7 for additional details regarding ongoing work to develop forward looking climate change scenarios.

## Table SCE 5-02
Table SCE 5-02: Summary of IWMS Risk Categories
Severe Risk Area (SRA) Criteria
Fire Risk Egress Constrained Areas – locations identified based on an index comprised of a high historical fire frequency and population/roadway egress. Additionally, a burn-in buffer around egress locations are modeled to determine which assets, if involved in an ignition would burn into egress locations within the simulated burn period.
Significant fire consequence – locations with the potential for greater than 10,000 acres burned based on wildfire simulations.
High winds – Locations, which if even fully covered with covered conductor, would still be subject to high PSPS likelihood.
Communities of Elevated Fire Concern (CEFCs) – Smaller geographic areas where terrain, construction, and other factors could lead to smaller, fast-moving fires threatening populated locations under benign (normal) weather conditions.
High Consequence Area (HCA) Criteria
Locations that do not meet any SRA criteria.
Destructive fire consequence – locations in which simulated wildfires exceed 300 acres.
Locations that have been subject to PSPS de-energizations.
Other HFRA Criteria
Locations that do not meet either SRA or HCA criteria.
Small fire consequence - locations with the potential for less than 300 acres burned based on wildfire simulations.

## Table SCE 5-02a
Table SCE 5-02a – Circuit Miles Per IWMS Risk Tranche
IWMS Risk Tranche | Approximate Circuit Miles
Severe Risk Areas | 3218
High Consequence Areas | 4466
Other HFRA | 1659
Total | 9343

## Table SCE 5-03
Table SCE 5-03: MARS Conversion Table
Attribute | Units | Weight | Range | Scaling Factor
Safety | Index | 50% | 0 - 100 | Linear
Reliability | Customer Minutes of Interruption (CMI) | 25% | 0 - 2 billion | Linear
Financial | Dollars | 25% | 0 - 5 billion | Linear

## Table SCE 5-04
Table SCE 5-04: Risk Models Containing Separate Modules
| Probability of Ignition | Wildfire Consequence (Technosylva)
Weather Analysis | No. Weather variables are not contained in a separate module for this model. Weather variables are attributes within the machine learning model. | Yes. Weather scenarios are modular in this model.
Fire Behavior Analysis | Not applicable, this model does not analyze or consider this element. | Yes. Fire Behavior Analysis is modular in this model.
Seasonal Vegetation Analysis | No. Vegetation variables are not contained in a separate module, they are attributes within the model. | Yes. Vegetation (i.e., fuel and fuel moisture) is modular in this model.
Equipment Failure | No. Equipment variables are not contained in a separate module for this model. They are attributes within the machine learning model. | Not applicable, this model does not analyze or consider this element.
Exposure and Vulnerability Analysis | Not applicable, this model does not analyze or consider this element. | Yes. HFRA (exposure) and AFN/NRCI (vulnerability) are separate components of this model

## Table SCE 5-05
Table SCE 5-05: Version Control
Models and software version controls aligned with industry standard programs, procedures, and protocols
Probability of Ignition | Yes. SCE maintains documentation and model information changes as new assets and features are updated in the model. Code commentary is updated as versions are changed.
Wildfire Consequence | Yes. SCE’s vendor maintains documentation and model information consistent with Energy Safety’s guidelines.
Version control of model input data, including geospatial data layers
Probability of Ignition | Yes. SCE reassesses and maintains POI models on an annual basis.
Wildfire Consequence | Yes. SCE reassesses and maintains wildfire consequence models on an biennial basis.
Procedures for updating technical, verification, and validation documentation
Probability of Ignition | SCE maintains documentation detailing changes, enhancements, and improvements made to our POI model, pursuant to its goals in RM-1. SCE is in the process of updating its documentation and is evaluating various standards to utilize to further refine and standardize our documentation.
Wildfire Consequence | Yes. SCE’s vendor maintains this information consistent with industry standard practice.

## Table 6-1
Table 6-1: List of Prioritized Areas in SCE’s Service Territory Based on Overall Utility Risk
Priority | Circuit Segment and/or Span ID | Length (miles) | Overall Utility Risk | Wildfire Risk | Outage Program Risk | Percent of Overall Utility Risk | Associated Risk Drivers
1 | SHOVEL_RAR0419_EOL | 25.4264 | 4.0312 | 4.0312 | 2.47e-05 | 1.513% | CFO Other Risk, EFF Risk
2 | SHOVEL_RAR0102_RCS0621 | 8.0923 | 2.5774 | 2.5774 | 7.83e-06 | 0.9672% | CFO Other Risk, EFF Risk
3 | FINGAL_CB_RAR0352 | 13.6666 | 2.4849 | 2.4849 | 5.79e-05 | 0.9325% | EFF Risk, CFO Other Risk
4 | DAVENPORT_RAR0051_EOL | 8.1939 | 2.4553 | 2.4552 | 2.54e-06 | 0.9214% | EFF Risk, CFO Other Risk
5 | DAVENPORT_RAR0050_RAR0586 | 9.4043 | 2.4027 | 2.4027 | 2.86e-06 | 0.9016% | EFF Risk, CFO Other Risk
6 | HUGHES LAKE_RAR0442_EOL | 22.9408 | 2.3169 | 2.3169 | 2.76e-05 | 0.8694% | EFF Risk, CFO Other Risk
7 | PASCAL_RAR1915_EOL | 9.8597 | 2.2616 | 2.2616 | 7.68e-05 | 0.8487% | EFF Risk, CFO Other Risk
8 | POPPET FLATS_CB_RAR0980 | 14.3789 | 2.1826 | 2.1825 | 6.88e-05 | 0.819% | EFF Risk, CFO Other Risk
9 | STONEMAN_CB_RCS7996 | 11.7697 | 2.1496 | 2.1496 | 8.15e-05 | 0.8067% | EFF Risk, CFO Other Risk
10 | KICKAPOO TRAIL_RCS0908_EOL | 30.4972 | 2.0757 | 2.0757 | 9.43e-05 | 0.7789% | EFF Risk, CFO Other Risk
11 | PHEASANT_CB_RAR0687 | 3.1022 | 2.042 | 2.042 | 6.62e-06 | 0.7663% | EFF Risk, CFO Other Risk
12 | DAVENPORT_RAR3480_RAR0050_RAR0051_ | 12.2279 | 2.0124 | 2.0124 | 3.72e-06 | 0.7552% | EFF Risk, CFO Other Risk
13 | DAVENPORT_RAR0173_EOL | 11.3805 | 1.9436 | 1.9436 | 3.48e-06 | 0.7294% | EFF Risk, CFO Other Risk
14 | SOPHIE_CB_EOL | 24.4248 | 1.9416 | 1.9416 | 4.23e-05 | 0.7286% | EFF Risk, CFO Other Risk
15 | BOOTLEGGER_RAR7203_RAR7134_PS0293_ | 13.591 | 1.8682 | 1.8682 | 1.8e-05 | 0.7011% | CFO Other Risk, EFF Risk
16 | WINERY_RAR1690_RAR1360 | 29.8267 | 1.8485 | 1.8485 | 2.44e-05 | 0.6937% | CFO Other Risk, EFF Risk
17 | POPPET FLATS_RAR0980_EOL | 15.9147 | 1.8224 | 1.8224 | 7.61e-05 | 0.6839% | EFF Risk, CFO Other Risk
18 | LUISENO_RAR1971_EOL | 13.0067 | 1.7726 | 1.7726 | 8.68e-08 | 0.6652% | CFO Other Risk, EFF Risk
19 | STORES_RAR1072_RAR1024_RAR0820_ | 7.5861 | 1.7529 | 1.7529 | 4.01e-05 | 0.6578% | EFF Risk, CFO Other Risk
20 | RAYBURN_PS2219_EOL | 4.9594 | 1.6993 | 1.6993 | 4.54e-05 | 0.6377% | EFF Risk, CFO Other Risk
21 | CHAWA_RAR1743_EOL | 31.5303 | 1.6836 | 1.6836 | 1.57e-05 | 0.6318% | EFF Risk, CFO Other Risk
22 | PIONEERTOWN_CB_RAR0423_RAR0409_ | 11.431 | 1.6722 | 1.6722 | 2.12e-05 | 0.6275% | EFF Risk, CFO Other Risk
23 | STORES_RAR1024_EOL | 9.2242 | 1.6459 | 1.6459 | 5.02e-05 | 0.6176% | EFF Risk, CFO Other Risk
24 | PIONEERTOWN_RCS0240_EOL | 12.2514 | 1.645 | 1.645 | 2.21e-05 | 0.6173% | EFF Risk, CFO Other Risk
25 | DAVENPORT_CB_RAR3480_RAR6564_ | 6.8137 | 1.557 | 1.557 | 2.08e-06 | 0.5843% | EFF Risk, CFO Other Risk
26 | CONDOR_RAR1573_EOL | 15.7407 | 1.5322 | 1.5322 | 2.19e-05 | 0.575% | EFF Risk, CFO Other Risk
27 | KICKAPOO TRAIL_RAR0241_RCS0908 | 12.4378 | 1.4695 | 1.4695 | 3.89e-05 | 0.5515% | EFF Risk, CFO Other Risk
28 | PICONI_CB_RAR7219 | 14.0815 | 1.4577 | 1.4577 | 0.00015905 | 0.547% | EFF Risk, CFO Other Risk
29 | PIONEERTOWN_RAR0423_RCS0239_RCS0240_ | 10.1632 | 1.4239 | 1.4239 | 1.89e-05 | 0.5344% | EFF Risk, CFO Other Risk
30 | FINGAL_RAR7077_EOL | 10.4384 | 1.4092 | 1.4092 | 4.46e-05 | 0.5288% | EFF Risk, CFO Other Risk
31 | DAVENPORT_RAR0586_EOL | 4.1891 | 1.3761 | 1.3761 | 1.28e-06 | 0.5164% | EFF Risk, CFO Other Risk
32 | PIONEERTOWN_RCS0239_EOL | 9.5111 | 1.3715 | 1.3715 | 1.72e-05 | 0.5147% | EFF Risk, CFO Other Risk
33 | BOOTLEGGER_RAR2010_EOL | 13.0394 | 1.278 | 1.278 | 1.72e-05 | 0.4796% | EFF Risk, CFO Other Risk
34 | ENERGY_PS5533_RAR1576_RAR0490_ | 3.7605 | 1.278 | 1.278 | 1.35e-05 | 0.4796% | CFO Other Risk, EFF Risk
35 | GNATCATCHER_RAR1540_RAR1524_RAR6463_ | 15.116 | 1.2532 | 1.2532 | 5.52e-05 | 0.4703% | EFF Risk, CFO Other Risk
36 | CHARDONNAY_CB_RCS1638 | 7.6974 | 1.2497 | 1.2497 | 2.27e-06 | 0.469% | EFF Risk, CFO Other Risk
37 | PAWNEE_RSR0724_RAR0264 | 12.2679 | 1.2432 | 1.2432 | 5.81e-05 | 0.4665% | CFO Other Risk, EFF Risk
38 | PICK_CB_RAR7157_RCS2190_PS1345 | 5.7924 | 1.2219 | 1.2219 | 1.47e-05 | 0.4585% | CFO Other Risk, EFF Risk
39 | PAWNEE_RSR1572_EOL | 13.8763 | 1.2074 | 1.2074 | 6.58e-05 | 0.4531% | EFF Risk, CFO Other Risk
40 | DAVENPORT_RAR6564_RAR0173 | 9.2294 | 1.19 | 1.19 | 2.82e-06 | 0.4466% | EFF Risk, CFO Other Risk
41 | ARAPAHO_RAR7929_EOL | 9.8083 | 1.1805 | 1.1805 | 4.03e-05 | 0.443% | CFO Other Risk, EFF Risk
42 | CONDOR_RAR1539_RAR0874_RAR1573_ | 8.6966 | 1.1779 | 1.1779 | 1.21e-05 | 0.442% | EFF Risk, CFO Other Risk
43 | SCHMIDT_RAR0057_EOL | 9.7719 | 1.1552 | 1.1552 | 4.64e-05 | 0.4335% | EFF Risk, CFO Other Risk
44 | SONOMA_RAR0470_EOL | 15.1418 | 1.1511 | 1.1511 | 1.22e-05 | 0.432% | EFF Risk, CFO Other Risk
45 | BOOTLEGGER_PS0293_EOL | 8.2799 | 1.1263 | 1.1263 | 1.09e-05 | 0.4227% | EFF Risk, CFO Other Risk
46 | PHEASANT_RAR0687_RAR2946 | 5.3915 | 1.1186 | 1.1186 | 1.15e-05 | 0.4198% | EFF Risk, CFO Other Risk
47 | BONANZA_CB_RAR0712 | 19.4734 | 1.1161 | 1.1161 | 3.9e-05 | 0.4188% | EFF Risk, CFO Other Risk
48 | PICK_RAR7157_EOL | 4.6722 | 1.0387 | 1.0387 | 1.18e-05 | 0.3898% | CFO Other Risk, EFF Risk
49 | STONEMAN_RCS7996_EOL | 13.0044 | 1.0358 | 1.0358 | 8.97e-05 | 0.3887% | CFO Other Risk, EFF Risk
50 | LOUCKS_CB_PS0444 | 3.6282 | 1.0228 | 1.0228 | 2.1e-06 | 0.3838% | EFF Risk, CFO Other Risk
51 | STARGLOW_RAR7401_RAR0954 | 16.0001 | 1.009 | 1.009 | 9.15e-05 | 0.3786% | EFF Risk, CFO Other Risk
52 | ERSKINE_RAR0716_EOL | 16.7815 | 1 | 0.99999 | 5.34e-05 | 0.3753% | EFF Risk, CFO Other Risk
53 | LASKER_PS0521_EOL | 11.2288 | 0.99875 | 0.99874 | 6.39e-05 | 0.3748% | EFF Risk, CFO Other Risk
54 | TITAN_RAR0909_EOL | 24.9989 | 0.97972 | 0.97971 | 3.74e-05 | 0.3677% | CFO Other Risk, EFF Risk
55 | DEALER_RAR0653_EOL | 8.341 | 0.96399 | 0.96398 | 5.68e-05 | 0.3617% | CFO Other Risk, EFF Risk
56 | CHAWA_CB_RAR1625_RAR7509_ | 5.7343 | 0.95105 | 0.95105 | 2.87e-06 | 0.3569% | CFO Other Risk, EFF Risk
57 | IDA_RAR0212_EOL | 5.9183 | 0.91345 | 0.91344 | 3.45e-05 | 0.3428% | EFF Risk, CFO Other Risk
58 | BOUQUET_CB_RAR6669_RAR7290_ | 7.5321 | 0.90635 | 0.90635 | 1.27e-05 | 0.3401% | EFF Risk, CFO Other Risk
59 | CASCADE_CB_EOL | 6.252 | 0.9037 | 0.9037 | 7.73e-05 | 0.3391% | CFO Other Risk, EFF Risk
60 | ENERGY_RAR1576_EOL | 7.4884 | 0.90314 | 0.90314 | 2.7e-05 | 0.3389% | EFF Risk, CFO Other Risk
61 | MAGUIRE_CB_RCS0205 | 14.4159 | 0.90263 | 0.90263 | 8.98e-06 | 0.3387% | EFF Risk, CFO Other Risk
62 | PICK_RCS2190_EOL | 4.6236 | 0.89844 | 0.89843 | 1.17e-05 | 0.3371% | CFO Other Risk, EFF Risk
63 | MORONGO_RAR0446_RAR1029 | 9.3585 | 0.8982 | 0.89819 | 1.04e-05 | 0.3371% | EFF Risk, CFO Other Risk
64 | KENO_RAR0819_EOL | 15.0374 | 0.89206 | 0.89206 | 1.88e-05 | 0.3348% | EFF Risk, CFO Other Risk
65 | CHAWA_RAR1625_RAR0255 | 14.3602 | 0.88257 | 0.88257 | 7.44e-06 | 0.3312% | EFF Risk, CFO Other Risk
66 | GAMBLER_RAR0134_RAR0098_PS0826_ | 17.6 | 0.8753 | 0.8753 | 4e-05 | 0.3285% | CFO Other Risk, EFF Risk
67 | GAMBLER_RAR0098_EOL | 14.1063 | 0.84132 | 0.84131 | 3.22e-05 | 0.3157% | CFO Other Risk, EFF Risk
68 | CHOLLA_CB_EOL | 12.231 | 0.82497 | 0.82497 | 3.62e-05 | 0.3096% | EFF Risk, CFO Other Risk
69 | WOBEGONE_RCS0847_EOL | 8.2036 | 0.82405 | 0.82405 | 4.82e-06 | 0.3092% | EFF Risk, CFO Other Risk
70 | VIENTO_RAR0118_RAR0306 | 24.4413 | 0.82066 | 0.82065 | 4.05e-05 | 0.308% | CFO Other Risk, EFF Risk
71 | CHARDONNAY_RAR1290_RSR8577 | 12.6868 | 0.81786 | 0.81786 | 3.75e-06 | 0.3069% | CFO Other Risk, EFF Risk
72 | FAYE_CB_RCS0683_RAR0675_ | 21.3297 | 0.81681 | 0.8168 | 5.39e-05 | 0.3065% | EFF Risk, CFO Other Risk
73 | CUDDEBACK_PS5611_RAR1098 | 15.3104 | 0.8114 | 0.81139 | 1.92e-05 | 0.3045% | CFO Other Risk, EFF Risk
74 | ATENTO_RAR7034_PS0673 | 6.747 | 0.80001 | 0.80001 | 6.49e-05 | 0.3002% | EFF Risk, CFO Other Risk
75 | CAMPANULA_RAR0622_EOL | 13.7549 | 0.798 | 0.798 | 0.00046874 | 0.2995% | EFF Risk, CFO Other Risk
76 | CAMPANULA_RAR0625_EOL | 6.8623 | 0.78484 | 0.78484 | 0.00023961 | 0.2945% | EFF Risk, CFO Other Risk
77 | PLACID_RAR0802_EOL | 14.6606 | 0.77611 | 0.77611 | 0.00031444 | 0.2912% | EFF Risk, CFO Other Risk
78 | GUFFY_RAR7187_EOL | 3.6443 | 0.77127 | 0.77127 | 2.11e-05 | 0.2894% | CFO Other Risk, EFF Risk
79 | PARADISE_RAR0735_RAR0739 | 8.0862 | 0.76781 | 0.76781 | 3.22e-05 | 0.2881% | EFF Risk, CFO Other Risk
80 | ENERGY_RAR0490_RCS5763-1_RAR0821_ | 3.457 | 0.75755 | 0.75754 | 1.24e-05 | 0.2843% | CFO Other Risk, EFF Risk
81 | WOBEGONE_RAR2321_RCS0847_RCS1092_ | 9.9756 | 0.74421 | 0.74421 | 5.86e-06 | 0.2793% | EFF Risk, CFO Other Risk
82 | PYTHON_RAR0066_RAR0036_RAR0038_ | 6.977 | 0.73627 | 0.73627 | 1.3e-05 | 0.2763% | EFF Risk, CFO Other Risk
83 | WINERY_CB_RAR7840_RAR1690_ | 7.6812 | 0.73425 | 0.73425 | 6.25e-06 | 0.2755% | CFO Other Risk, EFF Risk
84 | PAWNEE_RAR1568_EOL | 6.2754 | 0.71825 | 0.71825 | 2.97e-05 | 0.2695% | CFO Other Risk, EFF Risk
85 | ENERGY_RCS5770_EOL | 3.9772 | 0.71686 | 0.71686 | 1.43e-05 | 0.269% | EFF Risk, CFO Other Risk
86 | SHOVEL_CB_RAR3431_RAR0102_RAR0419 | 4.9087 | 0.71579 | 0.71579 | 4.76e-06 | 0.2686% | CFO Other Risk, EFF Risk
87 | PRONGHORN_RCS0028_EOL | 14.2039 | 0.69708 | 0.69707 | 5.44e-05 | 0.2616% | EFF Risk, CFO Other Risk
88 | BIG ROCK_RAR0104_RCS4050-1 | 3.3091 | 0.69529 | 0.69528 | 4.15e-05 | 0.2609% | CFO Other Risk, EFF Risk
89 | PICK_RAR7204_RAR0035 | 10.5518 | 0.69421 | 0.6942 | 2.67e-05 | 0.2605% | EFF Risk, CFO Other Risk
90 | METTLER_CB_RAR2199_RCS1132_ | 5.2509 | 0.6909 | 0.6909 | 1.06e-05 | 0.2593% | EFF Risk, CFO Other Risk
91 | KENO_CB_RAR0876_RAR1149_RAR0819_RAR0809__ | 11.471 | 0.68473 | 0.68472 | 1.71e-05 | 0.257% | EFF Risk, CFO Other Risk
92 | CANEBRAKE_CB_RAR0621_RAR0625_ | 14.5965 | 0.67049 | 0.67048 | 1.27e-05 | 0.2516% | CFO Other Risk, EFF Risk
93 | CONDOR_CB_RAR1539 | 8.8654 | 0.65969 | 0.65969 | 1.24e-05 | 0.2476% | CFO Other Risk, EFF Risk
94 | VIENTO_RAR5544_RAR0118 | 20.3376 | 0.65468 | 0.65467 | 3.37e-05 | 0.2457% | EFF Risk, CFO Other Risk
95 | BOOTLEGGER_PS0850_EOL | 4.7158 | 0.64432 | 0.64432 | 6.26e-06 | 0.2418% | EFF Risk, CFO Other Risk
96 | MORONGO_RSR0471_EOL | 8.9648 | 0.63628 | 0.63628 | 1.02e-05 | 0.2388% | EFF Risk, CFO Other Risk
97 | CORSAIR_RAR0284_EOL | 23.0356 | 0.62993 | 0.62992 | 0.00013812 | 0.2364% | EFF Risk, CFO Other Risk
98 | PIONEERTOWN_RAR0409_EOL | 11.4982 | 0.62947 | 0.62947 | 2.07e-05 | 0.2362% | EFF Risk, CFO Other Risk
99 | VICASA_CB_RAR5933_RAR0700_RAR0956 | 7.7133 | 0.62932 | 0.62932 | 3.78e-05 | 0.2362% | EFF Risk, CFO Other Risk
100 | HUGHES LAKE_RCS0277_EOL | 20.8518 | 0.62159 | 0.62158 | 2.5e-05 | 0.2333% | EFF Risk, CFO Other Risk
101 | NUTMEG_RCS1860_EOL | 5.5282 | 0.61922 | 0.61921 | 3.07e-05 | 0.2324% | EFF Risk, CFO Other Risk
102 | FLOODGATE_RAR1624_RCS0197 | 19.8566 | 0.61778 | 0.61777 | 4.03e-05 | 0.2318% | CFO Other Risk, EFF Risk
103 | PINTO_RAR0341_RCS1024 | 7.882 | 0.61413 | 0.61413 | 4.06e-08 | 0.2305% | EFF Risk, CFO Other Risk
104 | MORONGO_RAR0857_RSR0471 | 6.518 | 0.60702 | 0.60702 | 7.22e-06 | 0.2278% | EFF Risk, CFO Other Risk
105 | THACHER_RAR0096_RAR1164 | 16.021 | 0.60332 | 0.60332 | 2.74e-05 | 0.2264% | CFO Other Risk, EFF Risk
106 | EAGLE CREST_CB_EOL | 7.7444 | 0.5972 | 0.5972 | 6.36e-06 | 0.2241% | EFF Risk, CFO Other Risk
107 | CALIENTE_RAR1155_EOL | 12.3516 | 0.59221 | 0.59221 | 3.36e-05 | 0.2222% | EFF Risk, CFO Other Risk
108 | STORES_RAR0820_EOL | 4.0449 | 0.59198 | 0.59198 | 2.25e-05 | 0.2221% | EFF Risk, CFO Other Risk
109 | MUSTANG_RAR0619_EOL | 6.8366 | 0.58583 | 0.58582 | 8.43e-06 | 0.2198% | EFF Risk, CFO Other Risk
110 | CHAWA_RAR1603_EOL | 12.0815 | 0.58448 | 0.58448 | 6.03e-06 | 0.2193% | EFF Risk, CFO Other Risk
111 | METTLER_RAR2199_EOL | 16.1098 | 0.58048 | 0.58047 | 3.26e-05 | 0.2178% | EFF Risk, CFO Other Risk
112 | GNATCATCHER_RAR6463_EOL | 16.217 | 0.58024 | 0.58023 | 5.93e-05 | 0.2177% | EFF Risk, CFO Other Risk
113 | DEALER_CB_RAR1057 | 11.437 | 0.57861 | 0.57861 | 7.63e-05 | 0.2171% | EFF Risk, CFO Other Risk
114 | CACHUMA_RAR0078_RAR0598_RAR0563_ | 21.6637 | 0.57731 | 0.57729 | 0.00018141 | 0.2166% | CFO Other Risk, EFF Risk
115 | CHEVELLE_RCS0646_EOL | 6.8681 | 0.57498 | 0.57496 | 4e-05 | 0.2158% | EFF Risk, CFO Other Risk
116 | KIMDALE_RAR1716_RCS0856 | 16.819 | 0.57196 | 0.57196 | 2.05e-05 | 0.2146% | CFO Other Risk, EFF Risk
117 | SHOVEL_RAR3431_EOL | 1.7285 | 0.57124 | 0.57124 | 1.68e-06 | 0.2144% | CFO Other Risk, EFF Risk
118 | GILSTRAP_RAR0492_EOL | 10.4464 | 0.56983 | 0.56983 | 1.41e-07 | 0.2138% | CFO Other Risk, EFF Risk
119 | PURCHASE_CB_EOL | 3.2121 | 0.56434 | 0.56434 | 4.14e-06 | 0.2118% | EFF Risk, CFO Other Risk
120 | MOCKINGBIRD_CB_EOL | 6.477 | 0.56335 | 0.56334 | 3.31e-05 | 0.2114% | EFF Risk, CFO Other Risk
121 | ATENTO_RAR6933_EOL | 4.8114 | 0.56012 | 0.56012 | 4.66e-05 | 0.2102% | EFF Risk, CFO Other Risk
122 | RUSTIC_RAR6930_EOL | 4.9169 | 0.55772 | 0.55772 | 0.00013026 | 0.2093% | EFF Risk, CFO Other Risk
123 | BOUQUET_RAR6669_RAR0178 | 3.6621 | 0.55572 | 0.55572 | 5.99e-06 | 0.2085% | EFF Risk, CFO Other Risk
124 | HUCKLEBERRY_RCS0863_RAR0676 | 4.0774 | 0.55536 | 0.55536 | 2.06e-06 | 0.2084% | CFO Other Risk, EFF Risk
125 | KIMDALE_RCS0856_EOL | 17.294 | 0.55284 | 0.55283 | 2.14e-05 | 0.2075% | EFF Risk, CFO Other Risk
126 | HUGHES LAKE_RAR1546_EOL | 15.8421 | 0.55238 | 0.55237 | 1.91e-05 | 0.2073% | EFF Risk, CFO Other Risk
127 | HORNTOAD_RAR5088_RAR0536 | 4.55 | 0.55188 | 0.55187 | 2.6e-05 | 0.2071% | EFF Risk, CFO Other Risk
128 | LOPEZ_RAR0296_RAR0010 | 8.6517 | 0.5442 | 0.5442 | 2.96e-05 | 0.2042% | CFO Other Risk, EFF Risk
129 | HUCKLEBERRY_RAR0676_EOL | 9.4319 | 0.54268 | 0.54268 | 4.78e-06 | 0.2036% | EFF Risk, CFO Other Risk
130 | BOOTLEGGER_RCS1466_EOL | 6.357 | 0.54087 | 0.54087 | 8.37e-06 | 0.203% | EFF Risk, CFO Other Risk
131 | PICONI_RAR7219_EOL | 3.9105 | 0.5397 | 0.5397 | 4.42e-05 | 0.2025% | CFO Other Risk, EFF Risk
132 | MAGUIRE_RAR0117_EOL | 17.4322 | 0.53864 | 0.53863 | 1.07e-05 | 0.2021% | EFF Risk, CFO Other Risk
133 | SAND CANYON_RAR0290_EOL [1] | 8.1758 | 0.53117 | 0.53116 | 4.23e-05 | 0.1993% | EFF Risk, CFO Other Risk
134 | MENIFEE_RSR9228_EOL | 7.4061 | 0.52347 | 0.52347 | 6.52e-05 | 0.1964% | EFF Risk, CFO Other Risk
135 | NATIONS_RCS2254_EOL | 10.0879 | 0.51097 | 0.51097 | 8.83e-06 | 0.1917% | EFF Risk, CFO Other Risk
136 | TRUMPET_RAR0061_EOL | 9.268 | 0.50019 | 0.50018 | 7.4e-05 | 0.1877% | EFF Risk, CFO Other Risk
137 | TANAGER_RAR0708_EOL | 16.1483 | 0.49962 | 0.49961 | 3.28e-05 | 0.1875% | EFF Risk, CFO Other Risk
138 | GAMBLER_CB_RAR0134_RAR0005_ | 7.878 | 0.49719 | 0.49718 | 1.87e-05 | 0.1866% | CFO Other Risk, EFF Risk
139 | ERSKINE_RCS0634_RAR0632_RAR0716_ | 5.0717 | 0.49437 | 0.49437 | 1.69e-05 | 0.1855% | CFO Other Risk, EFF Risk
140 | CONDOR_RAR0874_RAR1542 | 5.0531 | 0.4899 | 0.4899 | 7.04e-06 | 0.1838% | EFF Risk, CFO Other Risk
141 | TAIWAN_RCS6128-3_PS1753 | 6.8527 | 0.48763 | 0.48762 | 2.42e-05 | 0.183% | EFF Risk, CFO Other Risk
142 | ACROBAT_RCS3323_PS0731 | 10.3532 | 0.48282 | 0.48281 | 8.41e-05 | 0.1812% | EFF Risk, CFO Other Risk
143 | STARGLOW_RAR0954_EOL | 5.3148 | 0.47811 | 0.47811 | 3.04e-05 | 0.1794% | EFF Risk, CFO Other Risk
144 | CALIENTE_RAR1070_EOL | 7.4699 | 0.47696 | 0.47695 | 2.03e-05 | 0.179% | CFO Other Risk, EFF Risk
145 | GRANNY SMITH_RAR7325_RAR0943 | 8.0707 | 0.46931 | 0.46931 | 9.5e-06 | 0.1761% | EFF Risk, CFO Other Risk
146 | LOPEZ_RAR3825_RAR0296 | 9.425 | 0.46836 | 0.46836 | 3.37e-05 | 0.1758% | EFF Risk, CFO Other Risk
147 | TUDOR_RAR7670_EOL | 5.8416 | 0.46552 | 0.46552 | 2.9e-05 | 0.1747% | EFF Risk, CFO Other Risk
148 | DEL CARBON_RAR0837_EOL | 4.4092 | 0.46433 | 0.46433 | 2.81e-05 | 0.1742% | EFF Risk, CFO Other Risk
149 | MENIFEE_CB_RCS7505-4_RSR9228_ | 9.5029 | 0.45458 | 0.45458 | 8.34e-05 | 0.1706% | EFF Risk, CFO Other Risk
150 | HELENKA_RCS7988_RAR7610 | 8.5428 | 0.45092 | 0.45092 | 2.56e-05 | 0.1692% | EFF Risk, CFO Other Risk
151 | FLYCATCHER_CB_RAR0658 | 3.4642 | 0.44939 | 0.44939 | 4.89e-06 | 0.1686% | CFO Other Risk, EFF Risk
152 | PYTHON_RAR0215_EOL | 3.3396 | 0.44686 | 0.44686 | 6.29e-06 | 0.1677% | EFF Risk, CFO Other Risk
153 | GAMBLER_RAR0005_EOL | 10.2695 | 0.43947 | 0.43947 | 2.36e-05 | 0.1649% | CFO Other Risk, EFF Risk
154 | SAND CANYON_RAR3410_RAR5051_RAR0290_RAR0191 | 4.5787 | 0.42723 | 0.42723 | 2.36e-05 | 0.1603% | CFO Other Risk, EFF Risk
155 | HELENKA_RAR7610_EOL | 7.7209 | 0.41878 | 0.41877 | 2.31e-05 | 0.1572% | EFF Risk, CFO Other Risk
156 | CHAWA_RAR0255_RAR1743_RAR1603_ | 14.3419 | 0.41565 | 0.41565 | 7.11e-06 | 0.156% | EFF Risk, CFO Other Risk
157 | BOOTLEGGER_RCS5646-3_RAR7203_RAR2010_PS0850 | 3.4179 | 0.41424 | 0.41424 | 4.36e-06 | 0.1554% | CFO Other Risk, EFF Risk
158 | CAMPANULA_RAR0640_RAR0611_RAR0622_ | 6.3289 | 0.41418 | 0.41418 | 0.00022945 | 0.1554% | EFF Risk, CFO Other Risk
159 | JELLYSTONE_RAR0412_EOL | 9.7587 | 0.41332 | 0.41331 | 3.07e-05 | 0.1551% | EFF Risk, CFO Other Risk
160 | RUSTIC_RAR3772_EOL | 3.0292 | 0.41304 | 0.41304 | 8.39e-05 | 0.155% | EFF Risk, CFO Other Risk
161 | CONDOR_RAR1542_EOL | 18.4465 | 0.40673 | 0.40673 | 2.57e-05 | 0.1526% | EFF Risk, CFO Other Risk
162 | PLATEAU_CB_RAR1173_RAR5090_ | 8.2184 | 0.40022 | 0.40021 | 6.66e-05 | 0.1502% | EFF Risk, CFO Other Risk
163 | SAND CANYON_RCS7480-1_EOL | 4.5344 | 0.39334 | 0.39334 | 2.34e-05 | 0.1476% | CFO Other Risk, EFF Risk
164 | MORGANSTEIN_RAR1360_BF35381_BF35380_RCS0506_BF35639_BF35382_ | 5.742 | 0.39333 | 0.39333 | 7.65e-05 | 0.1476% | EFF Risk, CFO Other Risk
165 | LIMITED_RAR0126_RCS0097 | 6.6115 | 0.38906 | 0.38905 | 0.00014713 | 0.146% | CFO Other Risk, EFF Risk
166 | MUSTANG_PS0615_RAR0904_RAR0668_RAR0619 | 8.0469 | 0.38887 | 0.38886 | 9.6e-06 | 0.1459% | CFO Other Risk, EFF Risk
167 | BLUE CUT_RSR0679_EOL | 12.3587 | 0.38461 | 0.3846 | 1.43e-05 | 0.1443% | EFF Risk, CFO Other Risk
168 | MUSTANG_RAR0668_EOL | 11.1435 | 0.38408 | 0.38407 | 1.42e-05 | 0.1441% | EFF Risk, CFO Other Risk
169 | PICK_PS1345_RAR7204 | 3.25 | 0.37979 | 0.37979 | 8.23e-06 | 0.1425% | CFO Other Risk, EFF Risk
170 | BOUQUET_RAR7290_BF59433 | 4.0795 | 0.37716 | 0.37716 | 6.68e-06 | 0.1415% | CFO Other Risk, EFF Risk
171 | CASTRO_CB_EOL | 17.0834 | 0.37638 | 0.37637 | 0.00015467 | 0.1412% | EFF Risk, CFO Other Risk
172 | DEALER_RAR1057_RAR0653_RAR0480_RAR1058 | 4.8265 | 0.37469 | 0.37468 | 3.54e-05 | 0.1406% | EFF Risk, CFO Other Risk
173 | BIG ROCK_CB_RAR0104 | 4.2599 | 0.37349 | 0.37348 | 5.33e-05 | 0.1402% | CFO Other Risk, EFF Risk
174 | STANWOOD_RAR0533_RCS0185 | 13.3383 | 0.37177 | 0.37176 | 9.95e-05 | 0.1395% | EFF Risk, CFO Other Risk
175 | PYTHON_RAR0038_EOL | 8.5831 | 0.37065 | 0.37064 | 1.63e-05 | 0.1391% | EFF Risk, CFO Other Risk
176 | RAYBURN_RAR1638_EOL | 2.7636 | 0.36607 | 0.36607 | 2.53e-05 | 0.1374% | EFF Risk, CFO Other Risk
177 | ATENTO_PS0402_RAR3342_RAR6933_RAR6932 | 3.5562 | 0.36145 | 0.36145 | 3.36e-05 | 0.1356% | EFF Risk, CFO Other Risk
178 | CALIENTE_CB_RAR1070_RAR1155_ | 6.3963 | 0.36121 | 0.36121 | 1.74e-05 | 0.1355% | CFO Other Risk, EFF Risk
179 | PENSTOCK_RSR1223_EOL | 10.2313 | 0.35848 | 0.35847 | 3.03e-05 | 0.1345% | CFO Other Risk, EFF Risk
180 | BENCH_PS0249_EOL | 2.9624 | 0.3552 | 0.3552 | 7.01e-06 | 0.1333% | EFF Risk, CFO Other Risk
181 | VIENTO_RAR0306_EOL | 21.9059 | 0.35418 | 0.35416 | 3.74e-05 | 0.1329% | EFF Risk, CFO Other Risk
182 | BALLOON_RAR1061_EOL | 3.1793 | 0.35396 | 0.35396 | 4.8e-05 | 0.1328% | EFF Risk, CFO Other Risk
183 | JELLYSTONE_RAR0439_EOL | 4.674 | 0.35258 | 0.35257 | 1.47e-05 | 0.1323% | EFF Risk, CFO Other Risk
184 | TANAGER_RAR6462_EOL | 14.6267 | 0.35115 | 0.35115 | 2.98e-05 | 0.1318% | EFF Risk, CFO Other Risk
185 | ARBORETUM_RAR0955_EOL [2] | 5.0047 | 0.35103 | 0.35102 | 2.68e-05 | 0.1317% | CFO Other Risk, EFF Risk
186 | KIMDALE_RAR1715_EOL | 13.79 | 0.34794 | 0.34794 | 1.7e-05 | 0.1306% | CFO Other Risk, EFF Risk
187 | GALAHAD_CB_RAR0767 | 4.2195 | 0.34548 | 0.34548 | 2.21e-05 | 0.1296% | EFF Risk, CFO Other Risk
188 | CERRITO_RAR8124_EOL | 1.6516 | 0.34529 | 0.34529 | 9.53e-05 | 0.1296% | EFF Risk, CFO Other Risk
189 | CANEBRAKE_RAR0621_RAR0630 | 9.3944 | 0.34526 | 0.34526 | 8.22e-06 | 0.1296% | EFF Risk, CFO Other Risk
190 | BRENNAN_RAR5082_GS0814-3_GS5105-2_ | 4.1472 | 0.34308 | 0.34307 | 3.56e-05 | 0.1287% | EFF Risk, CFO Other Risk
191 | TITAN_RAR0303_EOL | 18.0719 | 0.34231 | 0.34231 | 2.72e-05 | 0.1285% | EFF Risk, CFO Other Risk
192 | WESTBLUFF_RAR0013_EOL | 12.1035 | 0.34221 | 0.3422 | 4.33e-05 | 0.1284% | EFF Risk, CFO Other Risk
193 | MULHOLLAND_RAR0913_EOL | 11.2205 | 0.34114 | 0.34114 | 8.9e-06 | 0.128% | EFF Risk, CFO Other Risk
194 | BOOTLEGGER_RAR7134_RCS1466_RCS0835_ | 5.0105 | 0.34002 | 0.34002 | 6.68e-06 | 0.1276% | CFO Other Risk, EFF Risk
195 | MORONGO_RAR1029_EOL | 7.8989 | 0.33597 | 0.33596 | 8.91e-06 | 0.1261% | EFF Risk, CFO Other Risk
196 | SHEFFIELD_RAR0377_EOL | 8.3873 | 0.33593 | 0.33592 | 2.89e-05 | 0.1261% | EFF Risk, CFO Other Risk
197 | BENCH_RAR0268_RSR1003_PS1018_ | 5.5748 | 0.33541 | 0.33541 | 1.36e-05 | 0.1259% | EFF Risk, CFO Other Risk
198 | WOBEGONE_RCS1092_EOL | 3.2366 | 0.3351 | 0.3351 | 1.9e-06 | 0.1258% | EFF Risk, CFO Other Risk
199 | HORNTOAD_RCS0732_RAR5088_RCS1203-3_ | 3.1503 | 0.33504 | 0.33504 | 1.8e-05 | 0.1257% | EFF Risk, CFO Other Risk
200 | PAWNEE_RAR0264_RAR1571_RSR2274_ | 4.4127 | 0.33428 | 0.33428 | 2.09e-05 | 0.1254% | EFF Risk, CFO Other Risk
201 | VIENTO_RCS1726_RAR5544 | 8.2009 | 0.33296 | 0.33296 | 1.34e-05 | 0.1249% | CFO Other Risk, EFF Risk
202 | CARANCHO_RAR0798_EOL | 8.4781 | 0.332 | 0.332 | 3.39e-05 | 0.1246% | CFO Other Risk, EFF Risk
203 | CARANCHO_CB_RAR1675_RAR0798_RAR7280 | 5.4001 | 0.33076 | 0.33076 | 2.15e-05 | 0.1241% | CFO Other Risk, EFF Risk
204 | KENO_RAR0809_EOL | 8.734 | 0.33041 | 0.3304 | 2.43e-05 | 0.124% | CFO Other Risk, EFF Risk
205 | MUTUAL_GS0745-1_EOL | 3.7072 | 0.32999 | 0.32998 | 7.16e-05 | 0.1238% | CFO Other Risk, EFF Risk
206 | FINGAL_RAR0123_EOL | 4.5682 | 0.32758 | 0.32758 | 1.84e-05 | 0.1229% | EFF Risk, CFO Other Risk
207 | CUTHBERT_CB_RCS0919 | 1.7936 | 0.32363 | 0.32362 | 2.86e-05 | 0.1214% | EFF Risk, CFO Other Risk
208 | DRISKILL_RAR3883_RAR0063 | 10.5795 | 0.32338 | 0.32336 | 4.43e-05 | 0.1214% | EFF Risk, CFO Other Risk
209 | FINGAL_RAR0352_RAR7077_RAR0123_ | 4.0686 | 0.32264 | 0.32263 | 1.79e-05 | 0.1211% | EFF Risk, CFO Other Risk
210 | LOTTO_CB_EOL | 4.3528 | 0.3198 | 0.31979 | 1.53e-05 | 0.12% | EFF Risk, CFO Other Risk
211 | SAUNDERS_RAR0692_RCS0944 | 8.2417 | 0.31903 | 0.31902 | 2.99e-05 | 0.1197% | CFO Other Risk, EFF Risk
212 | DARTMOUTH_RSR9279_EOL | 5.7915 | 0.3119 | 0.31189 | 7.33e-05 | 0.117% | EFF Risk, CFO Other Risk
213 | CALIMESA_PS2944_EOL | 3.4425 | 0.31075 | 0.31075 | 2.69e-05 | 0.1166% | EFF Risk, CFO Other Risk
214 | JELLYSTONE_RCS0712_RAR0439_RAR0716_ | 6.8777 | 0.30863 | 0.30862 | 2.79e-05 | 0.1158% | EFF Risk, CFO Other Risk
215 | LUISENO_RAR1972_RAR0497 | 7.0588 | 0.3079 | 0.3079 | 5.05e-08 | 0.1155% | EFF Risk, CFO Other Risk
216 | KEENE_RAR0786_EOL | 30.4098 | 0.3056 | 0.30559 | 2.04e-05 | 0.1147% | CFO Other Risk, EFF Risk
217 | RIVA_CB_EOL | 26.9373 | 0.30395 | 0.30395 | 0.00019549 | 0.1141% | EFF Risk, CFO Other Risk
218 | GRANNY SMITH_RAR0943_RCS0056 | 3.5337 | 0.30359 | 0.30359 | 3.94e-06 | 0.1139% | EFF Risk, CFO Other Risk
219 | LACRESTA_CB_RCS1351_RCS7929_ | 5.8583 | 0.30326 | 0.30325 | 7.33e-06 | 0.1138% | CFO Other Risk, EFF Risk
220 | BIRCHIM_CB_RAR0164_RAR0207_ | 6.7038 | 0.30146 | 0.30145 | 9.54e-06 | 0.1131% | EFF Risk, CFO Other Risk
221 | MERLIN_CB_RCS3850_RAR0775_ | 3.9643 | 0.3011 | 0.3011 | 8.62e-06 | 0.113% | EFF Risk, CFO Other Risk
222 | GNATCATCHER_CB_RAR1540 | 7.7696 | 0.30064 | 0.30064 | 2.84e-05 | 0.1128% | EFF Risk, CFO Other Risk
223 | NORTHPARK_RAR2372_EOL | 7.6387 | 0.30029 | 0.30028 | 0.00010649 | 0.1127% | EFF Risk, CFO Other Risk
224 | PELONA_CB_EOL | 1.5585 | 0.2989 | 0.29888 | 8.14e-05 | 0.1122% | CFO Other Risk, EFF Risk
225 | TAPO_RAR6509_RAR6133_PS0046_ | 4.117 | 0.29862 | 0.29862 | 1.02e-05 | 0.1121% | EFF Risk, CFO Other Risk
226 | DYSART_RAR0278_RCS0290_RCS0746_ | 2.2863 | 0.29589 | 0.29589 | 3.32e-07 | 0.111% | CFO Other Risk, EFF Risk
227 | PLACID_RCS0407_RAR0802 | 8.1959 | 0.29489 | 0.29489 | 0.000178 | 0.1107% | EFF Risk, CFO Other Risk
228 | TENNECO_RAR0741_EOL | 17.3331 | 0.29409 | 0.29408 | 0.00013448 | 0.1104% | EFF Risk, CFO Other Risk
229 | PAWNEE_RSR2274_RAR1568 | 1.6391 | 0.29395 | 0.29395 | 7.75e-06 | 0.1103% | CFO Other Risk, EFF Risk
230 | BONANZA_RAR0712_PS0713 | 6.8147 | 0.29309 | 0.29308 | 1.38e-05 | 0.11% | EFF Risk, CFO Other Risk
231 | SCHMIDT_CB_RAR0057 | 3.684 | 0.29286 | 0.29286 | 1.73e-05 | 0.1099% | EFF Risk, CFO Other Risk
232 | LOUCKS_PS0444_EOL | 1.379 | 0.29207 | 0.29207 | 7.99e-07 | 0.1096% | CFO Other Risk, EFF Risk
233 | CHEVELLE_PME6582-2_RAR0810 | 4.0117 | 0.29188 | 0.29187 | 2.33e-05 | 0.1095% | EFF Risk, CFO Other Risk
234 | PATRICIA_RAR5140_RAR0360 | 11.0915 | 0.29145 | 0.29145 | 8.88e-05 | 0.1094% | EFF Risk, CFO Other Risk
235 | MAGUIRE_RAR0779_RAR0117 | 8.4048 | 0.28996 | 0.28996 | 5.2e-06 | 0.1088% | EFF Risk, CFO Other Risk
236 | IDA_RAR0861_RAR0212 | 1.6263 | 0.28941 | 0.28941 | 1.29e-05 | 0.1086% | EFF Risk, CFO Other Risk
237 | DYSART_RCS0746_RCS0912 | 3.3095 | 0.28748 | 0.28748 | 4.8e-07 | 0.1079% | EFF Risk, CFO Other Risk
238 | TENNECO_RAR0745_RAR0761_RAR3835_ | 13.8688 | 0.28729 | 0.28728 | 0.0001076 | 0.1078% | EFF Risk, CFO Other Risk
239 | KIMDALE_CB_RAR1716_RAR1715_ | 8.335 | 0.28603 | 0.28603 | 1.04e-05 | 0.1073% | CFO Other Risk, EFF Risk
240 | VERA CRUZ_RCS6376_RAR0870_RAR7515_ | 3.289 | 0.28188 | 0.28188 | 5.4e-06 | 0.1058% | EFF Risk, CFO Other Risk
241 | STANWOOD_RAR0395_EOL | 7.0953 | 0.27743 | 0.27742 | 5.45e-05 | 0.1041% | EFF Risk, CFO Other Risk
242 | KENO_RAR0876_EOL | 6.7628 | 0.27721 | 0.2772 | 8.26e-06 | 0.104% | EFF Risk, CFO Other Risk
243 | CHARDONNAY_RCS1638_RAR1290 | 2.0555 | 0.27644 | 0.27644 | 6.05e-07 | 0.1037% | CFO Other Risk, EFF Risk
244 | ROADRUNNER_PS0728_RAR2329 | 3.7281 | 0.27238 | 0.27238 | 2e-05 | 0.1022% | EFF Risk, CFO Other Risk
245 | ARAPAHO_CB_RAR7929 | 4.4965 | 0.27225 | 0.27225 | 1.86e-05 | 0.1022% | EFF Risk, CFO Other Risk
246 | TANAGER_RAR2220_RAR6462 | 8.5775 | 0.27058 | 0.27058 | 1.75e-05 | 0.1015% | EFF Risk, CFO Other Risk
247 | WINERY_RAR1360_EOL | 7.0327 | 0.26923 | 0.26923 | 5.72e-06 | 0.101% | EFF Risk, CFO Other Risk
248 | MORGANSTEIN_RAR5448_PS0471_PS0229_ | 7.6714 | 0.26645 | 0.26645 | 9.99e-05 | 0.09999% | EFF Risk, CFO Other Risk
249 | TIN MINE_RAR4801_EOL | 7.3425 | 0.26582 | 0.26582 | 7.83e-05 | 0.09975% | EFF Risk, CFO Other Risk
250 | HUGHES LAKE_RAR0121_RCS0277 | 10.6841 | 0.26537 | 0.26536 | 1.29e-05 | 0.09958% | EFF Risk, CFO Other Risk
251 | CHAWA_RAR7509_EOL | 4.3129 | 0.265 | 0.265 | 2.16e-06 | 0.09944% | EFF Risk, CFO Other Risk
252 | MUSTANG_RAR0904_EOL | 5.8293 | 0.26473 | 0.26473 | 7.14e-06 | 0.09934% | CFO Other Risk, EFF Risk
253 | DELUZ_CB_RAR7803 | 7.9016 | 0.26431 | 0.26431 | 2.17e-05 | 0.09918% | EFF Risk, CFO Other Risk
254 | OAKDALE_RAR7615_EOL | 9.8068 | 0.26414 | 0.26413 | 5.12e-05 | 0.09912% | EFF Risk, CFO Other Risk
255 | GRANNY SMITH_RCS0056_EOL | 9.8061 | 0.26371 | 0.26371 | 1.06e-05 | 0.09896% | CFO Other Risk, EFF Risk
256 | ERSKINE_RAR0900_EOL | 8.5656 | 0.25968 | 0.25968 | 2.71e-05 | 0.09745% | EFF Risk, CFO Other Risk
257 | HORNTOAD_CB_RCS0732 | 4.4659 | 0.25947 | 0.25947 | 2.52e-05 | 0.09737% | EFF Risk, CFO Other Risk
258 | FLOODGATE_RCS0197_PS1619 | 9.0701 | 0.25895 | 0.25894 | 1.88e-05 | 0.09717% | EFF Risk, CFO Other Risk
259 | PICK_RAR0035_EOL [1] | 10.2163 | 0.25826 | 0.25825 | 2.59e-05 | 0.09691% | CFO Other Risk, EFF Risk
260 | WESTBROOK_CB_EOL | 2.9729 | 0.25728 | 0.25728 | 8.31e-06 | 0.09655% | EFF Risk, CFO Other Risk
261 | FIREBIRD_RCS5485-1_RCS2000 | 3.4733 | 0.25581 | 0.25581 | 2.56e-05 | 0.096% | EFF Risk, CFO Other Risk
262 | MESA GRANDE_RCS1000_EOL | 6.0594 | 0.25538 | 0.25538 | 3.05e-05 | 0.09583% | EFF Risk, CFO Other Risk
263 | ARMADA_CB_GS5064-2 | 3.8849 | 0.25359 | 0.25358 | 7.02e-05 | 0.09516% | EFF Risk, CFO Other Risk
264 | PERRIS_CB_EOL | 3.0293 | 0.25296 | 0.25296 | 5.46e-05 | 0.09493% | EFF Risk, CFO Other Risk
265 | BUCKHORN_RAR0408_RAR0404_RAR0403_ | 16.2354 | 0.2524 | 0.25239 | 4.91e-05 | 0.09472% | EFF Risk, CFO Other Risk
266 | BURNT MOUNTAIN_RAR0721_EOL | 7.3234 | 0.2516 | 0.25158 | 1.91e-05 | 0.09441% | EFF Risk, CFO Other Risk
267 | TRUMPET_RAR3842_EOL | 10.2231 | 0.25026 | 0.25025 | 8.1e-05 | 0.09391% | EFF Risk, CFO Other Risk
268 | STAGELINE_CB_EOL | 10.8679 | 0.2492 | 0.24919 | 5.08e-05 | 0.09351% | CFO Other Risk, EFF Risk
269 | MAMBA_PME7428-1_RAR0043 | 4.1635 | 0.24909 | 0.24908 | 3.14e-05 | 0.09347% | CFO Other Risk, EFF Risk
270 | ARLENE_CB_PS0204 | 2.9497 | 0.24824 | 0.24824 | 7.14e-05 | 0.09316% | EFF Risk, CFO Other Risk
271 | ROS_PS1474_PME5303-4 | 7.6962 | 0.24807 | 0.24807 | 3.96e-05 | 0.09309% | EFF Risk, CFO Other Risk
272 | FERRARA_RAR0054_PS0587 | 1.9876 | 0.2468 | 0.24679 | 2.31e-05 | 0.09261% | CFO Other Risk, EFF Risk
273 | ESCALA_CB_EOL | 6.4478 | 0.24431 | 0.24431 | 3.15e-06 | 0.09168% | CFO Other Risk, EFF Risk
274 | BLACKFOOT_CB_EOL | 3.7545 | 0.24247 | 0.24246 | 3.92e-05 | 0.09099% | EFF Risk, CFO Other Risk
275 | ARCHIE_RAR1340_EOL | 9.6629 | 0.24235 | 0.24235 | 4.6e-08 | 0.09094% | EFF Risk, CFO Other Risk
276 | HASS_RAR0116_EOL | 8.9063 | 0.2416 | 0.2416 | 0.00015337 | 0.09066% | EFF Risk, CFO Other Risk
277 | RIM_RAR0273_EOL | 4.296 | 0.24019 | 0.24018 | 5.61e-05 | 0.09013% | EFF Risk, CFO Other Risk
278 | CEREAL_CB_RAR0998 | 4.3353 | 0.23979 | 0.23979 | 6.39e-06 | 0.08999% | EFF Risk, CFO Other Risk
279 | NORTHPARK_RAR0822_RAR2372_RCS2391_ | 6.9887 | 0.23887 | 0.23887 | 9.68e-05 | 0.08964% | EFF Risk, CFO Other Risk
280 | PARADISE_RAR0739_EOL | 3.7084 | 0.23879 | 0.23878 | 1.47e-05 | 0.08961% | EFF Risk, CFO Other Risk
281 | VICASA_RAR5933_RAR5087_RAR0711_RAR1706 | 9.0394 | 0.23799 | 0.23799 | 4.42e-05 | 0.08931% | EFF Risk, CFO Other Risk
282 | BLUE CUT_RAR0816_RSR0679 | 8.7286 | 0.23688 | 0.23687 | 9.79e-06 | 0.08889% | EFF Risk, CFO Other Risk
283 | TAPO_RAR6133_EOL | 3.6955 | 0.23597 | 0.23597 | 9.19e-06 | 0.08855% | EFF Risk, CFO Other Risk
284 | WILDOMAR_RCS1349_EOL | 3.5491 | 0.23591 | 0.23591 | 7.72e-09 | 0.08853% | CFO Other Risk, EFF Risk
285 | HURST_RAR0611_EOL | 6.9893 | 0.23492 | 0.23491 | 4.61e-05 | 0.08816% | EFF Risk, CFO Other Risk
286 | BODKIN_RCS0849_EOL | 1.5095 | 0.23424 | 0.23424 | 1.03e-05 | 0.0879% | EFF Risk, CFO Other Risk
287 | DICE_CB_RCS0390 | 2.605 | 0.23313 | 0.23313 | 4.34e-08 | 0.08748% | CFO Other Risk, EFF Risk
288 | CIRCLE_RCS1133_EOL | 8.8024 | 0.22982 | 0.22982 | 1.04e-05 | 0.08624% | EFF Risk, CFO Other Risk
289 | ROTEC_RAR7372_EOL | 2.4983 | 0.22927 | 0.22927 | 1.31e-05 | 0.08604% | EFF Risk, CFO Other Risk
290 | MERLIN_RAR0775_EOL | 7.2967 | 0.22861 | 0.22861 | 1.56e-05 | 0.08579% | EFF Risk, CFO Other Risk
291 | BARRINGTON_RAR7346_RAR0405 | 11.1429 | 0.22718 | 0.22717 | 1.04e-05 | 0.08525% | EFF Risk, CFO Other Risk
292 | SONOMA_CB_RAR0470 | 14.0829 | 0.22565 | 0.22564 | 1.15e-05 | 0.08468% | EFF Risk, CFO Other Risk
293 | CORSAIR_RAR0268_EOL | 6.7533 | 0.22345 | 0.22345 | 4.04e-05 | 0.08385% | EFF Risk, CFO Other Risk
294 | SHEFFIELD_RAR0183_RAR0374_RAR0377_ | 4.7682 | 0.22339 | 0.22338 | 1.61e-05 | 0.08383% | EFF Risk, CFO Other Risk
295 | ENERGY_CB_PS5533 | 3.0713 | 0.22236 | 0.22235 | 1.1e-05 | 0.08344% | EFF Risk, CFO Other Risk
296 | WOBEGONE_RAR2322_EOL | 3.4511 | 0.22217 | 0.22217 | 2.04e-06 | 0.08337% | EFF Risk, CFO Other Risk
297 | PAWNEE_CB_RSR1572_RSR0724_ | 4.1444 | 0.22164 | 0.22164 | 2.08e-05 | 0.08317% | EFF Risk, CFO Other Risk
298 | PAWNEE_RAR1571_EOL | 7.4797 | 0.22091 | 0.22091 | 3.54e-05 | 0.0829% | CFO Other Risk, EFF Risk
299 | NORTHPARK_RCS2391_EOL | 3.0202 | 0.22 | 0.22 | 4.18e-05 | 0.08256% | EFF Risk, CFO Other Risk
300 | STARGLOW_RAR1247_EOL | 5.012 | 0.21762 | 0.21761 | 2.95e-05 | 0.08166% | EFF Risk, CFO Other Risk
301 | CRUMNER_RSR5731_EOL | 4.9681 | 0.21631 | 0.2163 | 1.53e-05 | 0.08117% | EFF Risk, CFO Other Risk
302 | CONINE_RSR0661_RCS0159 | 3.5172 | 0.21576 | 0.21576 | 4.65e-05 | 0.08097% | EFF Risk, CFO Other Risk
303 | BOUQUET_RAR0178_EOL | 5.3459 | 0.21575 | 0.21575 | 9.38e-06 | 0.08096% | EFF Risk, CFO Other Risk
304 | JELLYSTONE_RAR0716_EOL | 5.6178 | 0.2154 | 0.2154 | 1.83e-05 | 0.08083% | EFF Risk, CFO Other Risk
305 | GNATCATCHER_RAR1524_EOL | 7.7755 | 0.21432 | 0.21432 | 2.88e-05 | 0.08043% | EFF Risk, CFO Other Risk
306 | TUDOR_CB_RAR7670 | 5.5194 | 0.21424 | 0.21424 | 2.8e-05 | 0.0804% | EFF Risk, CFO Other Risk
307 | TANAGER_CB_RAR2220_RAR2094_RAR0708 | 10.5644 | 0.21415 | 0.21415 | 2.16e-05 | 0.08036% | CFO Other Risk, EFF Risk
308 | SAND CANYON_CB_GS7835-3 | 1.665 | 0.21235 | 0.21235 | 7.02e-06 | 0.07969% | EFF Risk, CFO Other Risk
309 | BOOTLEGGER_RCS0835_RAR4268 | 10.7134 | 0.21196 | 0.21196 | 1.41e-05 | 0.07954% | EFF Risk, CFO Other Risk
310 | TUNGSTEN_CB_RAR0649_RAR0608_ | 0.75954 | 0.21173 | 0.2117 | 2.71e-05 | 0.07945% | EFF Risk, CFO Other Risk
311 | ARLENE_PS0204_RCS5558-4_GS2714-1_ | 2.3284 | 0.21025 | 0.21025 | 6.25e-05 | 0.0789% | EFF Risk, CFO Other Risk
312 | ENERGY_RCS5763-1_EOL | 0.28118 | 0.20926 | 0.20926 | 1.01e-06 | 0.07853% | CFO Other Risk, EFF Risk
313 | CANEBRAKE_RAR0630_EOL | 18.5258 | 0.20847 | 0.20846 | 1.63e-05 | 0.07823% | EFF Risk, CFO Other Risk
314 | CLYDESDALE_CB_EOL | 7.251 | 0.20799 | 0.20799 | 2.53e-05 | 0.07805% | EFF Risk, CFO Other Risk
315 | CALAMAR_CB_RCS1601 | 5.9479 | 0.20743 | 0.20743 | 1e-05 | 0.07784% | EFF Risk, CFO Other Risk
316 | KICKAPOO TRAIL_CB_RAR0241 | 5.1676 | 0.20679 | 0.20677 | 2.55e-05 | 0.0776% | EFF Risk, CFO Other Risk
317 | JELLYSTONE_CB_RCS0712_RAR0412_ | 7.8274 | 0.2025 | 0.20249 | 3.1e-05 | 0.07599% | EFF Risk, CFO Other Risk
318 | PENSTOCK_RAR1257_RSR1223 | 9.1183 | 0.20202 | 0.20201 | 2.67e-05 | 0.07581% | CFO Other Risk, EFF Risk
319 | TRUMPET_CB_RAR5949_RAR0061_RAR3842 | 4.8162 | 0.20116 | 0.20116 | 3.82e-05 | 0.07549% | EFF Risk, CFO Other Risk
320 | STARGLOW_RCS0959_EOL | 2.9944 | 0.19905 | 0.19905 | 1.73e-05 | 0.0747% | EFF Risk, CFO Other Risk
321 | BLUE CUT_RSR2535_EOL | 5.1025 | 0.19762 | 0.19762 | 5.74e-06 | 0.07416% | EFF Risk, CFO Other Risk
322 | CORINTH_RCS1100_EOL | 3.1325 | 0.1959 | 0.1959 | 5.37e-05 | 0.07351% | EFF Risk, CFO Other Risk
323 | HELENKA_RAR1232_RCS7988 | 4.9244 | 0.19559 | 0.19559 | 1.48e-05 | 0.0734% | EFF Risk, CFO Other Risk
324 | ENCHANTED_BF02306_EOL | 4.6188 | 0.19497 | 0.19496 | 1.03e-05 | 0.07316% | EFF Risk, CFO Other Risk
325 | MEMPHIS_RCS0414_EOL | 7.8127 | 0.19462 | 0.19462 | 0.00012407 | 0.07303% | EFF Risk, CFO Other Risk
326 | VERDUGO_RAR0900_RCS0124 | 5.9588 | 0.19193 | 0.19192 | 3.4e-05 | 0.07202% | EFF Risk, CFO Other Risk
327 | GALAHAD_RAR0654_EOL | 5.4938 | 0.19192 | 0.19192 | 2.91e-05 | 0.07202% | EFF Risk, CFO Other Risk
328 | TANAGER_RAR2094_EOL | 5.1056 | 0.19103 | 0.19103 | 1.04e-05 | 0.07169% | EFF Risk, CFO Other Risk
329 | ENERGY_RCS8085-2_RCS5841-1 | 1.5671 | 0.19002 | 0.19002 | 5.64e-06 | 0.07131% | CFO Other Risk, EFF Risk
330 | LASKER_CB_PS0521 | 4.5034 | 0.18851 | 0.1885 | 2.9e-05 | 0.07074% | EFF Risk, CFO Other Risk
331 | FARMINGTON_CB_RAR7452 | 5.2464 | 0.1875 | 0.1875 | 3.86e-05 | 0.07036% | EFF Risk, CFO Other Risk
332 | OMEGA_RAR0233_EOL | 5.6775 | 0.18748 | 0.18748 | 2.03e-05 | 0.07035% | CFO Other Risk, EFF Risk
333 | FLOODGATE_RAR0752_EOL | 5.699 | 0.18682 | 0.18682 | 1.22e-05 | 0.07011% | EFF Risk, CFO Other Risk
334 | LAKELAND_RAR7182_EOL | 7.7449 | 0.18613 | 0.18612 | 2.19e-05 | 0.06985% | EFF Risk, CFO Other Risk
335 | RUBIN_CB_RCS0030 | 4.0936 | 0.18589 | 0.18589 | 6.62e-05 | 0.06976% | CFO Other Risk, EFF Risk
336 | LUISENO_RAR0497_EOL | 4.8652 | 0.18392 | 0.18392 | 3.2e-08 | 0.06902% | EFF Risk, CFO Other Risk
337 | CEREAL_RAR0998_EOL | 4.3276 | 0.18383 | 0.18383 | 6.26e-06 | 0.06899% | CFO Other Risk, EFF Risk
338 | BUCKHORN_RAR0403_PS0553 | 12.4577 | 0.18345 | 0.18345 | 3.8e-05 | 0.06884% | EFF Risk, CFO Other Risk
339 | FERRARA_RAR0350_EOL | 4.2189 | 0.18343 | 0.18343 | 4.88e-05 | 0.06884% | EFF Risk, CFO Other Risk
340 | STUBBY_RSR0666_EOL | 0.8925 | 0.18304 | 0.18304 | 2.91e-08 | 0.06869% | CFO Other Risk, EFF Risk
341 | STORES_RCS5933-1_RAR1072 | 1.5174 | 0.18271 | 0.18271 | 8.1e-06 | 0.06857% | CFO Other Risk, EFF Risk
342 | CORSAIR_RAR0179_RAR1249_RAR0284_ | 21.3567 | 0.18205 | 0.18205 | 0.00012742 | 0.06832% | EFF Risk, CFO Other Risk
343 | CLOVE_CB_GS2528-3 | 5.1622 | 0.18155 | 0.18154 | 3.89e-05 | 0.06813% | EFF Risk, CFO Other Risk
344 | CUTHBERT_RAR8848_BF05638_BF35584_ | 3.5996 | 0.18038 | 0.18038 | 5.17e-05 | 0.06769% | EFF Risk, CFO Other Risk
345 | MCGEE_RCS0139_EOL | 7.2089 | 0.1794 | 0.17939 | 1.18e-05 | 0.06732% | EFF Risk, CFO Other Risk
346 | BURNT MOUNTAIN_CB_RAR0721 | 5.4938 | 0.17887 | 0.17885 | 2.44e-05 | 0.06712% | EFF Risk, CFO Other Risk
347 | SNOWCREEK_CB_EOL | 1.5812 | 0.17684 | 0.17684 | 1.29e-06 | 0.06636% | EFF Risk, CFO Other Risk
348 | PATRICIA_RAR0267_EOL | 10.2875 | 0.17518 | 0.17517 | 8.22e-05 | 0.06574% | EFF Risk, CFO Other Risk
349 | BLUE CUT_RAR0817_RSR2535 | 6.1914 | 0.17488 | 0.17488 | 7.31e-06 | 0.06563% | EFF Risk, CFO Other Risk
350 | INTAKE_CB_RCS0617 | 6.7549 | 0.17436 | 0.17436 | 3.76e-06 | 0.06543% | EFF Risk, CFO Other Risk
351 | SHOVEL_RCS0621_EOL | 1.2267 | 0.17376 | 0.17376 | 1.18e-06 | 0.0652% | CFO Other Risk, EFF Risk
352 | LACRESTA_RCS1351_EOL | 1.3248 | 0.17343 | 0.17343 | 1.65e-06 | 0.06508% | CFO Other Risk, EFF Risk
353 | VERDEMONT_RCS0796_RCS0833 | 7.6762 | 0.17323 | 0.17323 | 3.54e-07 | 0.065% | EFF Risk, CFO Other Risk
354 | MAGUIRE_RCS0205_RAR0779 | 8.0138 | 0.17223 | 0.17223 | 4.94e-06 | 0.06463% | CFO Other Risk, EFF Risk
355 | COVE_CB_RCS0315 | 2.8428 | 0.1713 | 0.1713 | 1.88e-05 | 0.06428% | EFF Risk, CFO Other Risk
356 | VICASA_RAR0711_EOL [3] | 5.1741 | 0.17016 | 0.17016 | 2.53e-05 | 0.06385% | EFF Risk, CFO Other Risk
357 | NICHOLAS_CB_RCS0678 | 1.9293 | 0.17014 | 0.17014 | 3.77e-05 | 0.06385% | EFF Risk, CFO Other Risk
358 | BENCH_PS0130_PS0916 | 2.7491 | 0.16991 | 0.16991 | 6.7e-06 | 0.06376% | EFF Risk, CFO Other Risk
359 | HACKBERRY_RAR0686_EOL | 5.0127 | 0.16871 | 0.16871 | 3.23e-05 | 0.06331% | CFO Other Risk, EFF Risk
360 | CUTHBERT_RAR8623_EOL | 1.6027 | 0.16678 | 0.16678 | 2.36e-05 | 0.06259% | EFF Risk, CFO Other Risk
361 | TRUMPET_RAR5949_EOL | 2.4761 | 0.16644 | 0.16644 | 1.96e-05 | 0.06246% | EFF Risk, CFO Other Risk
362 | TECOLOTE_RSR1573_EOL | 8.357 | 0.1659 | 0.16589 | 0.00013186 | 0.06226% | CFO Other Risk, EFF Risk
363 | DEL CARBON_CB_RAR0837 | 4.4191 | 0.16507 | 0.16507 | 2.71e-05 | 0.06194% | EFF Risk, CFO Other Risk
364 | TETLEY_RCS0671_EOL | 3.4176 | 0.16498 | 0.16498 | 2.48e-05 | 0.06191% | EFF Risk, CFO Other Risk
365 | TEJON_RAR0500_EOL | 14.8065 | 0.16353 | 0.16353 | 2.31e-05 | 0.06137% | EFF Risk, CFO Other Risk
366 | GORGE_RCS0545_RCS1064 [2] | 4.8135 | 0.16341 | 0.1634 | 3.97e-05 | 0.06132% | EFF Risk, CFO Other Risk
367 | PATRIOT_RAR0286_EOL | 3.9099 | 0.16299 | 0.16299 | 6.48e-05 | 0.06116% | EFF Risk, CFO Other Risk
368 | HILLFIELD_CB_RCS0471_RCS6452-3_ | 2.6432 | 0.16225 | 0.16224 | 4.65e-05 | 0.06089% | EFF Risk, CFO Other Risk
369 | ROMANUS_GS6031-2_EOL | 4.5758 | 0.16201 | 0.16201 | 8.1e-05 | 0.0608% | CFO Other Risk, EFF Risk
370 | KENO_RAR1149_EOL | 2.5097 | 0.16164 | 0.16163 | 5.6e-06 | 0.06066% | EFF Risk, CFO Other Risk
371 | STROSNIDER_CB_RAR0058 | 6.8967 | 0.16109 | 0.16109 | 3.19e-05 | 0.06045% | EFF Risk, CFO Other Risk
372 | PENSTOCK_PS0691_RCS0596 | 4.1946 | 0.16011 | 0.1601 | 1.22e-05 | 0.06008% | CFO Other Risk, EFF Risk
373 | VICASA_RAR0700_EOL | 3.2284 | 0.15975 | 0.15975 | 1.57e-05 | 0.05995% | EFF Risk, CFO Other Risk
374 | SDGE 520_CB_EOL | 2.0892 | 0.15964 | 0.15964 | 1.72e-07 | 0.05991% | EFF Risk, CFO Other Risk
375 | BERKSHIRE_CB_EOL | 5.0362 | 0.15957 | 0.15957 | 1.18e-06 | 0.05988% | CFO Other Risk, EFF Risk
376 | TRUMP_CB_EOL | 15.5789 | 0.15946 | 0.15945 | 8.89e-06 | 0.05984% | EFF Risk, CFO Other Risk
377 | NAPOLEON_PS0552_EOL | 1.196 | 0.15779 | 0.15779 | 5.61e-05 | 0.05921% | EFF Risk, CFO Other Risk
378 | ONAGA_RAR0853_RCS1022 | 5.3896 | 0.15636 | 0.15635 | 1.11e-05 | 0.05868% | EFF Risk, CFO Other Risk
379 | OAK GLEN_RAR0012_RAR0270 | 9.6908 | 0.15339 | 0.15338 | 3.12e-05 | 0.05756% | EFF Risk, CFO Other Risk
380 | COVENTRY_RCS0292_RCS0006 | 1.5659 | 0.15335 | 0.15335 | 8.75e-06 | 0.05755% | EFF Risk, CFO Other Risk
381 | BARRINGTON_RAR0405_EOL | 7.7667 | 0.15331 | 0.15331 | 7.2e-06 | 0.05753% | EFF Risk, CFO Other Risk
382 | ONBORD_RAR7254_RAR3750_RAR0348_ | 2.7611 | 0.15165 | 0.15165 | 7.69e-05 | 0.05691% | EFF Risk, CFO Other Risk
383 | NUTMEG_CB_RCS1860 | 1.5078 | 0.15109 | 0.15109 | 8.37e-06 | 0.0567% | EFF Risk, CFO Other Risk
384 | GREEN BEAR_CB_RAR2118 | 5.9748 | 0.151 | 0.15099 | 9.13e-05 | 0.05666% | EFF Risk, CFO Other Risk
385 | COVENTRY_RAR0008_EOL | 4.282 | 0.1509 | 0.1509 | 2.41e-05 | 0.05663% | EFF Risk, CFO Other Risk
386 | WAITE_PME2579-1_PS1872 | 3.7723 | 0.15016 | 0.15016 | 2.24e-05 | 0.05635% | EFF Risk, CFO Other Risk
387 | BLEDSOE_CB_RCS0496 | 16.0043 | 0.15014 | 0.15014 | 5.53e-06 | 0.05634% | CFO Other Risk, EFF Risk
388 | IDA_PS0486_RAR0861 | 2.1227 | 0.1498 | 0.1498 | 1.28e-05 | 0.05621% | EFF Risk, CFO Other Risk
389 | INYO LUMBER_CB_RAR0371_RCS0325_ | 1.6027 | 0.1485 | 0.14849 | 1.12e-05 | 0.05573% | EFF Risk, CFO Other Risk
390 | CHEVELLE_RAR0810_RCS0646 | 3.3647 | 0.14819 | 0.14818 | 1.95e-05 | 0.05561% | EFF Risk, CFO Other Risk
391 | HORNTOAD_RAR0536_PS0161_PS0747_ | 3.8874 | 0.14783 | 0.14783 | 2.22e-05 | 0.05548% | EFF Risk, CFO Other Risk
392 | WHIPSTOCK_RAR0140_EOL | 4.5652 | 0.14645 | 0.14645 | 1.98e-05 | 0.05496% | EFF Risk, CFO Other Risk
393 | THACHER_RAR3659_EOL | 6.6814 | 0.14591 | 0.14591 | 1.15e-05 | 0.05475% | EFF Risk, CFO Other Risk
394 | ZENDA_RCS2146_EOL | 14.0164 | 0.14564 | 0.14563 | 6.35e-06 | 0.05465% | CFO Other Risk, EFF Risk
395 | PINE COVE_RCS0069_RCS8993_RCS0380_ | 4.5798 | 0.14549 | 0.14549 | 2.9e-05 | 0.0546% | CFO Other Risk, EFF Risk
396 | DYSART_RCS0912_EOL | 1.3116 | 0.14399 | 0.14399 | 2e-07 | 0.05403% | EFF Risk, CFO Other Risk
397 | TENNECO_RAR0749_EOL | 17.8422 | 0.14389 | 0.14388 | 0.00015329 | 0.054% | EFF Risk, CFO Other Risk
398 | CASTRO_RCS1417_BF39171 | 6.3028 | 0.14323 | 0.14323 | 5.73e-05 | 0.05375% | CFO Other Risk, EFF Risk
399 | BROADCAST_CB_PS0905 | 10.4473 | 0.14044 | 0.14044 | 6.8e-07 | 0.0527% | CFO Other Risk, EFF Risk
400 | PRIMROSE_RAR0960_EOL | 5.5234 | 0.14015 | 0.14014 | 4.43e-05 | 0.05259% | CFO Other Risk, EFF Risk
401 | GRUWELL_RAR9237_PME4090-2 | 5.7092 | 0.13895 | 0.13895 | 3.34e-05 | 0.05214% | EFF Risk, CFO Other Risk
402 | PORCELAIN_CB_EOL | 4.7727 | 0.13881 | 0.13881 | 3.59e-06 | 0.05209% | EFF Risk, CFO Other Risk
403 | BENCH_PS1365_EOL | 0.74041 | 0.13876 | 0.13876 | 1.8e-06 | 0.05207% | EFF Risk, CFO Other Risk
404 | COVENTRY_RAR1224_EOL | 1.7771 | 0.13815 | 0.13815 | 9.94e-06 | 0.05184% | EFF Risk, CFO Other Risk
405 | GABBERT_RCS8821-4_EOL | 4.9694 | 0.13769 | 0.13767 | 5.53e-05 | 0.05167% | EFF Risk, CFO Other Risk
406 | CUTHBERT_RCS0036_BF02454_RAR0686_ | 2.8023 | 0.13707 | 0.13707 | 3.84e-05 | 0.05144% | EFF Risk, CFO Other Risk
407 | TAIWAN_RCS6128-1_EOL | 7.5414 | 0.13634 | 0.13634 | 2.65e-05 | 0.05116% | CFO Other Risk, EFF Risk
408 | SAUNDERS_RCS0948_RAR0692 | 4.3684 | 0.13617 | 0.13617 | 1.59e-05 | 0.0511% | EFF Risk, CFO Other Risk
409 | INVADER_RAR0962_EOL | 7.5065 | 0.13587 | 0.13586 | 1.74e-05 | 0.05099% | EFF Risk, CFO Other Risk
410 | SADDLEBACK_CB_PS0356 | 0.44511 | 0.13581 | 0.13581 | 1.77e-08 | 0.05096% | EFF Risk, CFO Other Risk
411 | AIDAN_GS7405-2_EOL | 2.1702 | 0.13539 | 0.13539 | 1.07e-05 | 0.05081% | EFF Risk, CFO Other Risk
412 | CROSSON_RAR1910_EOL | 7.892 | 0.13471 | 0.1347 | 0.00023327 | 0.05055% | CFO Other Risk, EFF Risk
413 | SDGE 521_CB_EOL | 2.8887 | 0.13438 | 0.13437 | 7.11e-08 | 0.05043% | EFF Risk, CFO Other Risk
414 | CONINE_RCS0159_GS2670-5 | 2.3078 | 0.13326 | 0.13326 | 3.12e-05 | 0.05001% | EFF Risk, CFO Other Risk
415 | MULHOLLAND_RCS0039_RAR0108_RAR0913_ | 2.5684 | 0.13319 | 0.13319 | 2.01e-06 | 0.04998% | EFF Risk, CFO Other Risk
416 | LUISENO_CB_RAR1971_RAR1972_ | 0.93087 | 0.13294 | 0.13294 | 1.61e-08 | 0.04989% | CFO Other Risk, EFF Risk
417 | SHEFFIELD_RAR0374_EOL | 4.1121 | 0.13063 | 0.13062 | 1.7e-05 | 0.04902% | EFF Risk, CFO Other Risk
418 | VICASA_RAR0956_EOL | 2.5913 | 0.12967 | 0.12967 | 1.26e-05 | 0.04866% | EFF Risk, CFO Other Risk
419 | ROS_RCS0807_EOL | 4.7078 | 0.12938 | 0.12938 | 2.38e-05 | 0.04855% | EFF Risk, CFO Other Risk
420 | FLYING D_RCS0708_EOL | 21.4905 | 0.12927 | 0.12927 | 1.94e-05 | 0.04851% | EFF Risk, CFO Other Risk
421 | RUSTIC_RAR3776_RCS0111 | 3.669 | 0.12917 | 0.12917 | 0.00010136 | 0.04847% | EFF Risk, CFO Other Risk
422 | STUBBY_RCS0707_RSR0666_RCS0671_ | 4.1282 | 0.12914 | 0.12914 | 1.3e-07 | 0.04846% | CFO Other Risk, EFF Risk
423 | PENSTOCK_RAR0065_PS0643_PS0641_BF76025_PS0691__ | 6.6649 | 0.12873 | 0.12872 | 1.9e-05 | 0.04831% | CFO Other Risk, EFF Risk
424 | GAMBLER_PS0826_EOL | 2.6672 | 0.12852 | 0.12852 | 7.42e-06 | 0.04823% | EFF Risk, CFO Other Risk
425 | LA MANCHA_RCS4062_EOL | 4.331 | 0.12764 | 0.12764 | 5.9e-05 | 0.0479% | EFF Risk, CFO Other Risk
426 | TAHQUITZ_RAR0141_RCS0559 | 3.6216 | 0.12764 | 0.12764 | 2.42e-06 | 0.0479% | EFF Risk, CFO Other Risk
427 | JAKE_CB_EOL | 2.7391 | 0.12669 | 0.12669 | 3.19e-07 | 0.04754% | EFF Risk, CFO Other Risk
428 | PHOTON_RCS8418-5_EOL | 16.9858 | 0.12663 | 0.12663 | 2.05e-05 | 0.04752% | CFO Other Risk, EFF Risk
429 | CHARDONNAY_RSR8577_EOL | 12.5978 | 0.12629 | 0.12629 | 3.71e-06 | 0.04739% | EFF Risk, CFO Other Risk
430 | MAYER_CB_RAR7937 | 5.5453 | 0.126 | 0.126 | 1.31e-08 | 0.04728% | EFF Risk, CFO Other Risk
431 | WHIPSTOCK_CB_RAR0030_RSR1302_RAR0140_RAR0351__ | 4.2547 | 0.12586 | 0.12586 | 1.83e-05 | 0.04723% | CFO Other Risk, EFF Risk
432 | ROADRUNNER_RAR2329_EOL | 3.9187 | 0.12564 | 0.12563 | 2.12e-05 | 0.04715% | EFF Risk, CFO Other Risk
433 | GABBERT_CB_RCS8821-4_PME6314-4_RCS4077-2 | 2.8135 | 0.1255 | 0.12549 | 3.11e-05 | 0.0471% | EFF Risk, CFO Other Risk
434 | PAYNE_RAR0970_EOL | 2.6534 | 0.12514 | 0.12514 | 2.51e-05 | 0.04696% | EFF Risk, CFO Other Risk
435 | BIG ROCK_RCS4050-1_EOL | 5.0784 | 0.12502 | 0.12501 | 5.89e-05 | 0.04691% | EFF Risk, CFO Other Risk
436 | SERRA_RCS0151_EOL | 4.0245 | 0.1242 | 0.1242 | 1.83e-06 | 0.04661% | EFF Risk, CFO Other Risk
437 | RUSTIC_GS3770-1_RAR6930_RAR3772_RAR3776 | 1.4252 | 0.12371 | 0.12371 | 3.68e-05 | 0.04642% | EFF Risk, CFO Other Risk
438 | MCGEE_CB_RCS0139 | 8.0214 | 0.12365 | 0.12364 | 1.31e-05 | 0.0464% | EFF Risk, CFO Other Risk
439 | SIENNA_GS0421-2_RCS0121-3 | 3.4408 | 0.12247 | 0.12247 | 1.3e-05 | 0.04596% | EFF Risk, CFO Other Risk
440 | CEDAR PINES_RCS0799_EOL | 1.4085 | 0.12227 | 0.12227 | 7.88e-06 | 0.04588% | EFF Risk, CFO Other Risk
441 | COVENTRY_RCS0006_RAR0008 | 2.7775 | 0.12205 | 0.12204 | 1.57e-05 | 0.0458% | EFF Risk, CFO Other Risk
442 | SADDLEBACK_PS0356_RCS1333 | 2.2854 | 0.12193 | 0.12193 | 4.97e-08 | 0.04576% | EFF Risk, CFO Other Risk
443 | NEARGATE_RAR0044_EOL | 4.9934 | 0.12086 | 0.12083 | 0.00025682 | 0.04536% | EFF Risk, CFO Other Risk
444 | TICO_RCS0362_RAR0736 | 10.3116 | 0.12072 | 0.12072 | 4.84e-05 | 0.0453% | EFF Risk, CFO Other Risk
445 | JARVIS_RAR0993_PS4129_PS1456_ | 3.8167 | 0.12038 | 0.12037 | 9.57e-06 | 0.04517% | EFF Risk, CFO Other Risk
446 | FERRARA_RCS2019_RAR0054 | 2.6644 | 0.12029 | 0.12029 | 3.27e-05 | 0.04514% | EFF Risk, CFO Other Risk
447 | CONESTOGA_PS1934_EOL | 5.507 | 0.12016 | 0.12015 | 3.68e-05 | 0.04509% | EFF Risk, CFO Other Risk
448 | BARRINGTON_RAR1187_EOL | 3.6032 | 0.11958 | 0.11958 | 3.33e-06 | 0.04488% | EFF Risk, CFO Other Risk
449 | COVENTRY_RAR1055_RCS0292 | 3.4986 | 0.11942 | 0.11941 | 1.94e-05 | 0.04481% | EFF Risk, CFO Other Risk
450 | BENCH_RSR1003_PS0130_PS0249_PS1365 | 1.1266 | 0.11881 | 0.11881 | 2.74e-06 | 0.04459% | CFO Other Risk, EFF Risk
451 | TRIUNFO_RAR4570_EOL | 2.9578 | 0.11809 | 0.11809 | 1.59e-05 | 0.04432% | EFF Risk, CFO Other Risk
452 | TRAUTWEIN_RAR0306_EOL | 4.4405 | 0.11794 | 0.11794 | 1.43e-05 | 0.04426% | EFF Risk, CFO Other Risk
453 | GARBONI_CB_EOL | 5.3152 | 0.11789 | 0.11789 | 3.08e-05 | 0.04424% | EFF Risk, CFO Other Risk
454 | CLARINET_RAR0299_EOL | 2.0292 | 0.11757 | 0.11757 | 1.32e-05 | 0.04412% | EFF Risk, CFO Other Risk
455 | CALIBER_RAR0041_EOL | 5.2336 | 0.1174 | 0.1174 | 1.19e-05 | 0.04405% | CFO Other Risk, EFF Risk
456 | LANE_RAR0919_EOL | 2.0641 | 0.11732 | 0.11731 | 6.93e-06 | 0.04402% | EFF Risk, CFO Other Risk
457 | JOB_CB_EOL | 5.6916 | 0.11726 | 0.11726 | 1.7e-05 | 0.044% | EFF Risk, CFO Other Risk
458 | PARADISE_CB_RAR0735 | 1.7463 | 0.11601 | 0.11601 | 6.92e-06 | 0.04354% | EFF Risk, CFO Other Risk
459 | CALIMESA_CB_PS2944 | 5.1112 | 0.11585 | 0.11585 | 4.13e-05 | 0.04347% | EFF Risk, CFO Other Risk
460 | PYTHON_RAR0036_EOL | 0.96295 | 0.11581 | 0.11581 | 1.82e-06 | 0.04346% | EFF Risk, CFO Other Risk
461 | RANKIN_CB_PS0909 | 6.9922 | 0.11522 | 0.11522 | 3.09e-06 | 0.04324% | EFF Risk, CFO Other Risk
462 | TITAN_RCS1271_RAR0265_RAR0303_ | 6.5818 | 0.11504 | 0.11504 | 8.48e-06 | 0.04317% | EFF Risk, CFO Other Risk
463 | BUFFER_CB_RAR0801 | 2.8906 | 0.11476 | 0.11475 | 4.87e-05 | 0.04306% | EFF Risk, CFO Other Risk
464 | WOBEGONE_RAR0437_EOL | 4.4703 | 0.11433 | 0.11433 | 2.73e-06 | 0.0429% | EFF Risk, CFO Other Risk
465 | WILDOMAR_RCS0923_RAR0925 | 2.6408 | 0.11418 | 0.11418 | 5.81e-09 | 0.04285% | CFO Other Risk, EFF Risk
466 | ASHLEY_CB_EOL | 2.5589 | 0.11405 | 0.11404 | 7.93e-06 | 0.0428% | EFF Risk, CFO Other Risk
467 | PINE COVE_RAR9115_RAR0218 | 4.8877 | 0.11311 | 0.11311 | 3.1e-05 | 0.04245% | EFF Risk, CFO Other Risk
468 | GALAHAD_RAR0650_RCS0658 | 8.0736 | 0.11262 | 0.11262 | 4.19e-05 | 0.04226% | EFF Risk, CFO Other Risk
469 | WILDOMAR_CB_RCS0923 | 5.036 | 0.11242 | 0.11242 | 1.19e-08 | 0.04219% | EFF Risk, CFO Other Risk
470 | PLATEAU_RAR5090_RAR0051 | 5.2308 | 0.11236 | 0.11236 | 4.24e-05 | 0.04217% | EFF Risk, CFO Other Risk
471 | ROUNDEL_RCS0065_EOL | 2.7323 | 0.11192 | 0.11192 | 5.95e-05 | 0.042% | EFF Risk, CFO Other Risk
472 | MILO_RAR0210_EOL | 3.112 | 0.11157 | 0.11157 | 8.68e-05 | 0.04187% | EFF Risk, CFO Other Risk
473 | MULHOLLAND_CB_RCS0039_RAR0108_RAR0913 | 5.9463 | 0.11144 | 0.11144 | 4.74e-06 | 0.04182% | EFF Risk, CFO Other Risk
474 | CRUZ_RCS1805_EOL | 1.725 | 0.11131 | 0.11131 | 3.67e-05 | 0.04177% | EFF Risk, CFO Other Risk
475 | HURST_RAR0317_RCS0216_RCS0378_ | 8.7597 | 0.11124 | 0.11123 | 6.01e-05 | 0.04174% | EFF Risk, CFO Other Risk
476 | CALGROVE_CB_RAR0071 | 6.9544 | 0.1107 | 0.11069 | 2.75e-05 | 0.04154% | EFF Risk, CFO Other Risk
477 | HORIZON_RAR3846_EOL | 7.3041 | 0.10967 | 0.10967 | 6.21e-05 | 0.04116% | CFO Other Risk, EFF Risk
478 | BUTTERFIELD_RCS5430-2_EOL | 6.4933 | 0.10846 | 0.10845 | 0.00011921 | 0.0407% | CFO Other Risk, EFF Risk
479 | SUTT_PS0898_552939ET1 | 3.6894 | 0.10811 | 0.1081 | 3.43e-05 | 0.04057% | EFF Risk, CFO Other Risk
480 | SERRA_PS0760_PS0243 | 5.9554 | 0.10785 | 0.10785 | 2.83e-06 | 0.04047% | EFF Risk, CFO Other Risk
481 | DRISKILL_RAR0063_EOL | 3.569 | 0.1076 | 0.1076 | 1.48e-05 | 0.04038% | CFO Other Risk, EFF Risk
482 | GUST_RAR6457_EOL | 5.3163 | 0.10757 | 0.10757 | 3.19e-05 | 0.04037% | CFO Other Risk, EFF Risk
483 | MACIEL_RCS3829-4_EOL | 2.0706 | 0.10754 | 0.10754 | 2.34e-05 | 0.04036% | EFF Risk, CFO Other Risk
484 | ROWCO_RAR0041_EOL | 8.8987 | 0.1075 | 0.10748 | 0.00023073 | 0.04034% | EFF Risk, CFO Other Risk
485 | POULTRY_RAR0182_BF01589 | 5.8315 | 0.10703 | 0.10703 | 2.47e-05 | 0.04016% | EFF Risk, CFO Other Risk
486 | BOA_CB_EOL | 2.1684 | 0.10693 | 0.10693 | 0.00012942 | 0.04013% | EFF Risk, CFO Other Risk
487 | SNOW VALLEY_RAR0610_RAR0605 | 5.3521 | 0.1069 | 0.1069 | 0.00010056 | 0.04012% | EFF Risk, CFO Other Risk
488 | SPICE_CB_PME6115-1 | 3.8942 | 0.10665 | 0.10664 | 2.48e-05 | 0.04002% | EFF Risk, CFO Other Risk
489 | LIMITED_RCS0097_EOL | 3.9147 | 0.10563 | 0.10563 | 8.85e-05 | 0.03964% | EFF Risk, CFO Other Risk
490 | ZONE_CB_RCS2381 | 4.5653 | 0.10562 | 0.10562 | 7.86e-06 | 0.03964% | EFF Risk, CFO Other Risk
491 | HUCKLEBERRY_CB_EOL | 1.8927 | 0.10558 | 0.10558 | 1.16e-06 | 0.03962% | EFF Risk, CFO Other Risk
492 | NAPOLEON_RAR0932_EOL | 2.6443 | 0.10515 | 0.10515 | 0.00012336 | 0.03946% | EFF Risk, CFO Other Risk
493 | TOLA_GS5826-3_EOL | 3.4659 | 0.10455 | 0.10455 | 3.8e-05 | 0.03923% | EFF Risk, CFO Other Risk
494 | STUBBY_RAR0670_RCS0526 | 3.9827 | 0.10412 | 0.10412 | 1.3e-07 | 0.03907% | EFF Risk, CFO Other Risk
495 | GALAHAD_RAR0767_RAR0654_RAR0652_ | 6.6947 | 0.10401 | 0.10401 | 3.5e-05 | 0.03903% | EFF Risk, CFO Other Risk
496 | URBITA_RAR1170_RCS0167 | 5.5034 | 0.10372 | 0.10372 | 1.75e-05 | 0.03892% | EFF Risk, CFO Other Risk
497 | MUSTANG_PS0648_EOL | 4.8326 | 0.10334 | 0.10333 | 5.88e-06 | 0.03878% | EFF Risk, CFO Other Risk
498 | HOOLIGAN_RCS4059-1_EOL | 3.7767 | 0.10301 | 0.103 | 3.95e-05 | 0.03866% | EFF Risk, CFO Other Risk
499 | DOMIC_CB_PS0041_PS0536_ | 5.2182 | 0.10276 | 0.10276 | 1.16e-05 | 0.03856% | CFO Other Risk, EFF Risk
500 | FERRARA_PS0587_RAR0350 | 5.6664 | 0.10265 | 0.10264 | 6.45e-05 | 0.03852% | EFF Risk, CFO Other Risk
501 | JEEP_RAR0355_EOL | 10.9622 | 0.10208 | 0.10206 | 5.16e-05 | 0.03831% | EFF Risk, CFO Other Risk
502 | PETIT_RAR2546_EOL | 4.2599 | 0.10132 | 0.10132 | 4.32e-06 | 0.03802% | EFF Risk, CFO Other Risk
503 | STRATHERN_CB_RCS0606 | 4.0845 | 0.10123 | 0.10121 | 7.19e-05 | 0.03799% | EFF Risk, CFO Other Risk
504 | KLEVEN_RCS2491-3_EOL | 1.3642 | 0.10112 | 0.10112 | 3.63e-05 | 0.03795% | EFF Risk, CFO Other Risk
505 | COLLIER_RAR0294_EOL | 1.8786 | 0.10069 | 0.10069 | 1.55e-05 | 0.03779% | EFF Risk, CFO Other Risk
506 | ROCKCREEK_CB_EOL | 11.4494 | 0.1001 | 0.10009 | 1.06e-05 | 0.03756% | EFF Risk, CFO Other Risk
507 | SPARLING_CB_EOL | 4.8288 | 0.099961 | 0.099956 | 3.86e-05 | 0.03751% | EFF Risk, CFO Other Risk
508 | CAMPANULA_RAR0611_EOL | 1.3404 | 0.099737 | 0.099735 | 5.24e-05 | 0.03743% | EFF Risk, CFO Other Risk
509 | OMEGA_RAR0393_EOL | 3.4261 | 0.099646 | 0.099646 | 1.22e-05 | 0.03739% | CFO Other Risk, EFF Risk
510 | GRANNY SMITH_CB_RAR7325 | 3.1519 | 0.099611 | 0.099611 | 3.48e-06 | 0.03738% | EFF Risk, CFO Other Risk
511 | WINERY_RAR7840_EOL | 3.11 | 0.099239 | 0.099238 | 2.53e-06 | 0.03724% | EFF Risk, CFO Other Risk
512 | MAMBA_RAR0043_BF59313 | 4.5572 | 0.098239 | 0.098232 | 3.46e-05 | 0.03687% | EFF Risk, CFO Other Risk
513 | TETLEY_RCS0667_RCS0671_RCS0668_ | 4.1482 | 0.097882 | 0.097876 | 3.01e-05 | 0.03673% | EFF Risk, CFO Other Risk
514 | STAR ROCK_RAR0092_EOL | 0.98286 | 0.097094 | 0.097091 | 2.93e-05 | 0.03644% | EFF Risk, CFO Other Risk
515 | TICO_RAR0736_EOL | 8.0286 | 0.097038 | 0.097033 | 3.86e-05 | 0.03641% | EFF Risk, CFO Other Risk
516 | PINTO_RCS1024_EOL | 2.1655 | 0.096978 | 0.096978 | 9.96e-09 | 0.03639% | CFO Other Risk, EFF Risk
517 | BUCKHORN_RSR3065_RAR0408 | 5.6774 | 0.096856 | 0.096853 | 1.74e-05 | 0.03635% | EFF Risk, CFO Other Risk
518 | VERA CRUZ_RAR7515_EOL | 1.4685 | 0.096284 | 0.096283 | 2.5e-06 | 0.03613% | EFF Risk, CFO Other Risk
519 | STAR ROCK_RAR7369_GS2845-3 | 0.95063 | 0.096201 | 0.096198 | 2.84e-05 | 0.0361% | CFO Other Risk, EFF Risk
520 | CHILLON_CB_EOL | 7.768 | 0.096176 | 0.096169 | 4.24e-05 | 0.03609% | EFF Risk, CFO Other Risk
521 | REJADA_RCS0538_RCS0183-3_RCS0183-2_ | 1.5143 | 0.096096 | 0.096093 | 9.7e-06 | 0.03606% | EFF Risk, CFO Other Risk
522 | ENERGY_RAR0012_RCS5770 | 0.69817 | 0.096073 | 0.096072 | 2.51e-06 | 0.03605% | CFO Other Risk, EFF Risk
523 | ATENTO_RAR7221_EOL | 0.54934 | 0.09509 | 0.09509 | 7.58e-06 | 0.03568% | CFO Other Risk, EFF Risk
524 | CLUB OAKS_RAR3133_EOL | 5.8905 | 0.094965 | 0.094965 | 0 | 0.03564% | EFF Risk, CFO Other Risk
525 | HAMMOCK_RCS0348_EOL | 7.9778 | 0.094648 | 0.094648 | 5.76e-07 | 0.03552% | EFF Risk, CFO Other Risk
526 | LIMITED_RCS1108_RAR0126 | 2.3715 | 0.094551 | 0.094548 | 5.5e-05 | 0.03548% | EFF Risk, CFO Other Risk
527 | SEAFORTH_RAR0111_EOL | 3.6465 | 0.094154 | 0.09415 | 1.15e-05 | 0.03533% | CFO Other Risk, EFF Risk
528 | RIDGE_PS0714_EOL | 3.6256 | 0.093979 | 0.093977 | 3.66e-06 | 0.03527% | EFF Risk, CFO Other Risk
529 | LYONS_RCS0058_EOL | 3.2219 | 0.093642 | 0.093639 | 6.07e-05 | 0.03514% | EFF Risk, CFO Other Risk
530 | SAUNDERS_RAR9121_RAR0134_RAR8932_RCS7314 | 2.4034 | 0.093318 | 0.093317 | 8.72e-06 | 0.03502% | EFF Risk, CFO Other Risk
531 | ACAPULCO_CB_RAR0750 | 1.3095 | 0.093284 | 0.093284 | 1.89e-07 | 0.03501% | EFF Risk, CFO Other Risk
532 | EASTER_RCS1196_RCS6480-3 | 2.03 | 0.093284 | 0.093284 | 1.21e-05 | 0.03501% | CFO Other Risk, EFF Risk
533 | MORGANSTEIN_PS0229_EOL | 1.1174 | 0.093067 | 0.093066 | 1.51e-05 | 0.03492% | EFF Risk, CFO Other Risk
534 | SKINNER_CB_PS1343 | 2.1665 | 0.092866 | 0.092866 | 1.29e-10 | 0.03485% | EFF Risk, CFO Other Risk
535 | RAINBOW_RAR2137_RCS1736 | 4.3581 | 0.092847 | 0.092847 | 5.12e-06 | 0.03484% | EFF Risk, CFO Other Risk
536 | VIDEO_RAR0927_EOL [2] | 6.5695 | 0.092089 | 0.092087 | 2.91e-05 | 0.03456% | EFF Risk, CFO Other Risk
537 | SAUNDERS_RAR8932_EOL | 7.5117 | 0.092026 | 0.092022 | 2.73e-05 | 0.03453% | EFF Risk, CFO Other Risk
538 | SAUNDERS_RCS0944_EOL | 2.0921 | 0.091816 | 0.091815 | 7.59e-06 | 0.03446% | EFF Risk, CFO Other Risk
539 | GULL LAKE_CB_EOL | 4.9047 | 0.091745 | 0.09173 | 3.58e-05 | 0.03443% | EFF Risk, CFO Other Risk
540 | MEMPHIS_RAR0234_EOL | 1.701 | 0.091559 | 0.091559 | 2.67e-05 | 0.03436% | CFO Other Risk, EFF Risk
541 | CRESTLINE_RAR0708_RAR1076 | 3.0358 | 0.091246 | 0.091243 | 3.43e-05 | 0.03424% | EFF Risk, CFO VEG Risk
542 | TEJON_RCS1316_PS0528 | 8.8636 | 0.09122 | 0.091218 | 1.36e-05 | 0.03423% | CFO Other Risk, EFF Risk
543 | CUTHBERT_RCS0919_RAR8848_RCS5486_RAR8623 | 0.86258 | 0.091164 | 0.091162 | 1.23e-05 | 0.03421% | EFF Risk, CFO Other Risk
544 | AVIATOR_RAR0534_EOL | 10.9053 | 0.091126 | 0.091125 | 5.62e-05 | 0.0342% | EFF Risk, CFO Other Risk
545 | RUSTIC_RCS0111_EOL | 3.6582 | 0.090953 | 0.090952 | 9.42e-05 | 0.03413% | CFO Other Risk, EFF Risk
546 | PETIT_RSR7187_RAR1452_RAR2546_ | 2.2808 | 0.090749 | 0.090748 | 3.13e-06 | 0.03405% | EFF Risk, CFO Other Risk
547 | MATILIJA_CB_RAR0329 | 9.4556 | 0.090449 | 0.090448 | 6.06e-05 | 0.03394% | EFF Risk, CFO Other Risk
548 | ZENDA_RCS0309_RCS2146_RCS2147_ | 4.7999 | 0.09029 | 0.090289 | 2.17e-06 | 0.03388% | EFF Risk, CFO Other Risk
549 | CORTESE_CB_RCS1234 | 0.96166 | 0.089068 | 0.089067 | 5.25e-06 | 0.03342% | EFF Risk, CFO Other Risk
550 | INYO LUMBER_RCS0325_EOL | 0.94306 | 0.088694 | 0.088693 | 4.6e-06 | 0.03328% | EFF Risk, CFO Other Risk
551 | MARCUS_GS0034-3_EOL | 5.8722 | 0.088557 | 0.088549 | 6.32e-05 | 0.03323% | EFF Risk, CFO Other Risk
552 | CALIBER_RAR0034_EOL | 7.5327 | 0.088539 | 0.088537 | 1.74e-05 | 0.03323% | CFO Other Risk, EFF Risk
553 | NEPAL_RAR0320_EOL | 2.788 | 0.088406 | 0.088404 | 4.9e-06 | 0.03318% | CFO Other Risk, EFF Risk
554 | TAGGERT_RAR0499_RAR0623 | 6.6071 | 0.088179 | 0.088173 | 8.39e-05 | 0.03309% | EFF Risk, CFO Other Risk
555 | ROS_RSR7085_RCS0807_PS1474_ | 4.3932 | 0.088135 | 0.088132 | 2.49e-05 | 0.03307% | EFF Risk, CFO Other Risk
556 | SERRA_CB_PS0760 | 3.1956 | 0.087991 | 0.08799 | 1.52e-06 | 0.03302% | EFF Risk, CFO Other Risk
557 | CASSIDY_RAR0470_EOL | 1.1757 | 0.08759 | 0.087587 | 2.84e-05 | 0.03287% | CFO Other Risk, EFF Risk
558 | KELLER_CB_PS9306 | 0.97989 | 0.087326 | 0.087326 | 3.22e-05 | 0.03277% | EFF Risk, CFO Other Risk
559 | MEDAL_RCS0502-4_RSR0178 | 8.9209 | 0.087296 | 0.087295 | 0.00017472 | 0.03276% | EFF Risk, CFO Other Risk
560 | CADENA_CB_RCS4021 | 1.1613 | 0.087102 | 0.087101 | 4.56e-05 | 0.03269% | EFF Risk, CFO Other Risk
561 | BAYLINER_CB_EOL | 2.7644 | 0.087076 | 0.087074 | 7.72e-05 | 0.03268% | EFF Risk, CFO Other Risk
562 | LOPEZ_RAR0010_EOL | 1.8457 | 0.086975 | 0.086974 | 6.14e-06 | 0.03264% | EFF Risk, CFO Other Risk
563 | MORGANSTEIN_CB_RAR1360_RAR5448_ | 1.3394 | 0.086542 | 0.086541 | 1.83e-05 | 0.03248% | CFO Other Risk, EFF Risk
564 | CALSTATE_RAR0868_EOL | 2.4424 | 0.086331 | 0.086331 | 0.00021135 | 0.0324% | EFF Risk, CFO Other Risk
565 | SEAWOLF_CB_PME6507-2_GS7436-2_ | 0.69487 | 0.085823 | 0.085822 | 1.73e-05 | 0.03221% | EFF Risk, CFO Other Risk
566 | GALAHAD_RAR3693_RCS0648 | 4.9223 | 0.085575 | 0.085572 | 2.58e-05 | 0.03211% | EFF Risk, CFO Other Risk
567 | DARTMOUTH_RCS1093_RAR7488 | 1.0925 | 0.085057 | 0.085057 | 1.36e-05 | 0.03192% | EFF Risk, CFO Other Risk
568 | BORCHARD_RAR0115_EOL | 1.4295 | 0.084236 | 0.084235 | 9.23e-06 | 0.03161% | EFF Risk, CFO Other Risk
569 | CORTESE_RCS1234_EOL | 0.96193 | 0.084169 | 0.084169 | 5.25e-06 | 0.03159% | CFO Other Risk, EFF Risk
570 | PRIMROSE_RAR0961_EOL | 2.7779 | 0.084166 | 0.084164 | 2.21e-05 | 0.03158% | CFO Other Risk, EFF Risk
571 | HUCKLEBERRY_CB_RCS0863_RAR1384_ | 4.4325 | 0.083724 | 0.083723 | 2.37e-06 | 0.03142% | CFO Other Risk, EFF Risk
572 | CARBINE_RAR0243_EOL | 1.9607 | 0.083563 | 0.083563 | 8.56e-06 | 0.03136% | EFF Risk, CFO Other Risk
573 | RIM_CB_RAR0273_RAR0274_RAR0341 | 3.0054 | 0.08345 | 0.083446 | 3.88e-05 | 0.03132% | EFF Risk, CFO Other Risk
574 | CEDAR GLEN_RAR0267_EOL | 4.5173 | 0.083424 | 0.083414 | 3.33e-05 | 0.03131% | EFF Risk, CFO Other Risk
575 | SAUNDERS_RCS7314_RCS0948 | 3.15 | 0.083229 | 0.083228 | 1.14e-05 | 0.03123% | EFF Risk, CFO Other Risk
576 | CARRIAGE_RAR0345_EOL | 4.4562 | 0.083005 | 0.083002 | 4.53e-05 | 0.03115% | EFF Risk, CFO Other Risk
577 | VERDUGO_RCS0124_PS0618 | 1.9974 | 0.082651 | 0.08265 | 1.14e-05 | 0.03102% | CFO Other Risk, EFF Risk
578 | CEDAR GLEN_RAR0390_EOL | 3.8896 | 0.082403 | 0.082394 | 2.86e-05 | 0.03092% | EFF Risk, CFO Other Risk
579 | TOLL_CB_RAR0216 | 2.4911 | 0.082177 | 0.082174 | 7.34e-06 | 0.03084% | EFF Risk, CFO Other Risk
580 | INTERPACE_RAR6470_RCS0063 | 4.2908 | 0.082116 | 0.082116 | 1.85e-07 | 0.03082% | EFF Risk, CFO Other Risk
581 | ALPINE_RAR0005_EOL | 2.1717 | 0.082112 | 0.08211 | 1.39e-05 | 0.03081% | EFF Risk, CFO Other Risk
582 | GRENADE_GS5166-2_EOL | 1.4072 | 0.081917 | 0.081916 | 2.65e-06 | 0.03074% | EFF Risk, CFO Other Risk
583 | ATENTO_RAR6932_RSR6971 | 0.52346 | 0.081734 | 0.081734 | 4.94e-06 | 0.03067% | EFF Risk, CFO Other Risk
584 | GUITAR_CB_RCS0317 | 7.1806 | 0.081401 | 0.0814 | 9.79e-06 | 0.03055% | EFF Risk, CFO Other Risk
585 | CACHUMA_RAR0598_PS0474 | 10.7768 | 0.080916 | 0.080908 | 9.02e-05 | 0.03036% | CFO Other Risk, EFF Risk
586 | ROUNDEL_RCS2288-2_RCS0065 | 1.2587 | 0.08077 | 0.080768 | 2.76e-05 | 0.03031% | EFF Risk, CFO Other Risk
587 | CARDINAL_CB_EOL | 5.2233 | 0.080696 | 0.080687 | 4.49e-05 | 0.03028% | EFF Risk, CFO Other Risk
588 | UTE_CB_EOL | 0.91717 | 0.080641 | 0.080641 | 4.09e-08 | 0.03026% | EFF Risk, CFO Other Risk
589 | ANTON_CB_RAR0621_RAR0217_ | 1.7418 | 0.080606 | 0.080606 | 8.45e-07 | 0.03025% | EFF Risk, CFO Other Risk
590 | TAHQUITZ_RCS0559_EOL | 6.3671 | 0.080534 | 0.080532 | 4.46e-06 | 0.03022% | EFF Risk, CFO Other Risk
591 | BLACKBURN_CB_GS3704-1 | 3.0652 | 0.080148 | 0.080144 | 0.00027427 | 0.03008% | EFF Risk, CFO Other Risk
592 | CANET_CB_RCS4272-4 | 13.3553 | 0.079439 | 0.079421 | 6.47e-05 | 0.02981% | EFF Risk, CFO Other Risk
593 | CRESCENTA_RCS0643_RCS0622 | 8.9423 | 0.079359 | 0.079349 | 0.00010521 | 0.02978% | EFF Risk, CFO Other Risk
594 | MERLIN_RCS3850_RAR0775 | 4.7089 | 0.079346 | 0.079344 | 1.01e-05 | 0.02978% | EFF Risk, CFO Other Risk
595 | TORONTO_CB_RAR0535_RAR0872_ | 5.3533 | 0.079148 | 0.079141 | 5.18e-05 | 0.0297% | EFF Risk, CFO Other Risk
596 | HIGH SCHOOL_RAR0042_EOL | 1.7526 | 0.079027 | 0.079026 | 3.24e-06 | 0.02966% | EFF Risk, CFO Other Risk
597 | TENNECO_CB_RAR0746_RAR0741_RAR0745 | 4.6758 | 0.078742 | 0.078739 | 3.63e-05 | 0.02955% | EFF Risk, CFO Other Risk
598 | CARANCHO_RAR1675_RAR9274 | 2.3011 | 0.078385 | 0.078385 | 9.14e-06 | 0.02941% | EFF Risk, CFO Other Risk
599 | GRAHAM_RAR0125_EOL | 2.3562 | 0.078298 | 0.078298 | 9.17e-05 | 0.02938% | EFF Risk, CFO Other Risk
600 | UNDERWOOD_CB_RCS0179_RAR0201_ | 2.591 | 0.078018 | 0.078016 | 3.91e-06 | 0.02928% | EFF Risk, CFO Other Risk
601 | CUTHBERT_RAR0686_EOL | 5.0183 | 0.077762 | 0.077755 | 6.87e-05 | 0.02918% | EFF Risk, CFO Other Risk
602 | COTTAGE GROVE_CB_EOL | 1.9767 | 0.077719 | 0.077716 | 1.41e-05 | 0.02916% | EFF Risk, CFO Other Risk
603 | SHOWDOWN_CB_GS6861-4 | 3.6911 | 0.077434 | 0.077422 | 2.99e-05 | 0.02906% | CFO Other Risk, EFF Risk
604 | APPALOUSA_CB_RAR7506 | 2.3267 | 0.077144 | 0.077143 | 1.36e-05 | 0.02895% | EFF Risk, CFO Other Risk
605 | NORTH SHORE_CB_RAR1121 | 1.4719 | 0.077138 | 0.077134 | 2.78e-05 | 0.02895% | EFF Risk, CFO Other Risk
606 | TICO_CB_RCS0362_PS0048_ | 5.9281 | 0.07647 | 0.076467 | 2.76e-05 | 0.0287% | EFF Risk, CFO Other Risk
607 | VERDUGO_PS0618_EOL | 4.8567 | 0.075741 | 0.075737 | 2.75e-05 | 0.02842% | CFO Other Risk, EFF Risk
608 | SAUNDERS_RCS0985_EOL | 2.7859 | 0.075731 | 0.07573 | 1.01e-05 | 0.02842% | EFF Risk, CFO Other Risk
609 | NEARGATE_CB_RAR0044_GS8466-1_ | 4.352 | 0.075517 | 0.075493 | 0.00021768 | 0.02834% | EFF Risk, CFO Other Risk
610 | TACKLE_RSR9167_EOL | 0.95867 | 0.075419 | 0.075419 | 8.15e-06 | 0.0283% | EFF Risk, CFO Other Risk
611 | LANGER_RCS0096_RAR0023 | 2.5347 | 0.075347 | 0.075345 | 2.52e-05 | 0.02828% | EFF Risk, CFO Other Risk
612 | STUBBY_RCS0671_EOL | 0.28548 | 0.075066 | 0.075066 | 9.21e-09 | 0.02817% | CFO Other Risk, EFF Risk
613 | ECHO_RAR0826_EOL | 1.8396 | 0.074752 | 0.074751 | 6.35e-06 | 0.02805% | EFF Risk, CFO Other Risk
614 | LEVECHE_RSR0479_EOL | 1.918 | 0.074605 | 0.074601 | 1.45e-05 | 0.028% | CFO Other Risk, EFF Risk
615 | SEMINARY_CB_RCS1828 | 4.8996 | 0.074597 | 0.074595 | 1.93e-05 | 0.02799% | EFF Risk, CFO Other Risk
616 | CARANCHO_RAR7280_EOL | 5.7459 | 0.074337 | 0.074336 | 2.28e-05 | 0.0279% | CFO Other Risk, EFF Risk
617 | MOCCASIN_CB_EOL | 6.6821 | 0.073567 | 0.073562 | 6e-05 | 0.02761% | EFF Risk, CFO Other Risk
618 | CARANCHO_RAR9274_EOL | 4.7419 | 0.073162 | 0.073161 | 1.88e-05 | 0.02745% | EFF Risk, CFO Other Risk
619 | RESORT_RAR1461_EOL | 3.1668 | 0.073045 | 0.073045 | 1e-07 | 0.02741% | EFF Risk, CFO Other Risk
620 | OAK KNOLL_RAR0044_EOL | 3.6523 | 0.072988 | 0.072984 | 7.7e-05 | 0.02739% | EFF Risk, CFO Other Risk
621 | ONBORD_RAR0348_EOL | 1.6128 | 0.072925 | 0.072923 | 4.51e-05 | 0.02737% | CFO Other Risk, EFF Risk
622 | CRESTLINE_RAR0021_PS2041 | 2.3139 | 0.072657 | 0.072654 | 2.61e-05 | 0.02727% | EFF Risk, CFO VEG Risk
623 | MAYBELL_RCS0867_EOL | 9.1998 | 0.072469 | 0.072468 | 1.6e-05 | 0.0272% | EFF Risk, CFO Other Risk
624 | THACHER_RAR5062_EOL | 3.1424 | 0.072451 | 0.07245 | 5.35e-06 | 0.02719% | EFF Risk, CFO Other Risk
625 | MIDDLE ROAD_RAR1109_EOL | 15.0712 | 0.072003 | 0.072001 | 1.55e-05 | 0.02702% | CFO Other Risk, EFF Risk
626 | WHIPSTOCK_RAR0145_EOL | 2.7043 | 0.07198 | 0.07198 | 1.17e-05 | 0.02701% | EFF Risk, CFO Other Risk
627 | ACRES_CB_RCS0515-1 | 1.4016 | 0.07133 | 0.071329 | 4.64e-05 | 0.02677% | EFF Risk, CFO Other Risk
628 | THACHER_RAR0174_EOL | 6.2335 | 0.071297 | 0.071295 | 1.06e-05 | 0.02676% | EFF Risk, CFO Other Risk
629 | BUCKNER_CB_EOL | 7.6154 | 0.071203 | 0.071199 | 8.7e-05 | 0.02672% | EFF Risk, CFO Other Risk
630 | AVENIDA_CB_GS2133-4_RAR0301_ | 5.0352 | 0.070981 | 0.070977 | 0.00015352 | 0.02664% | EFF Risk, CFO Other Risk
631 | STARGLOW_GS7098-1_RAR1247_RAR7502_ | 2.412 | 0.070528 | 0.070527 | 1.4e-05 | 0.02647% | EFF Risk, CFO Other Risk
632 | DONLON_CB_RAR0231_RAR3474_RAR0011 | 4.3702 | 0.070504 | 0.070502 | 1.18e-05 | 0.02646% | EFF Risk, CFO Other Risk
633 | SUTT_RAR0825_PS0898 | 2.1354 | 0.070225 | 0.070222 | 1.98e-05 | 0.02635% | EFF Risk, CFO Other Risk
634 | ROCKHILL_RAR1142_EOL | 7.5361 | 0.070098 | 0.070098 | 1.56e-05 | 0.02631% | EFF Risk, CFO Other Risk
635 | ZONE_RAR0475_EOL | 4.5006 | 0.069162 | 0.069161 | 7.69e-06 | 0.02595% | EFF Risk, CFO Other Risk
636 | SUTT_RAR0939_RAR0899_RAR0825_ | 5.8417 | 0.069139 | 0.069127 | 5.9e-05 | 0.02595% | EFF Risk, CFO Other Risk
637 | ROCKWELL_CB_EOL | 6.1463 | 0.069072 | 0.06906 | 5.32e-05 | 0.02592% | EFF Risk, CFO Other Risk
638 | LAMANDA_RCS1836_EOL [2] | 4.9521 | 0.06904 | 0.069034 | 4.51e-05 | 0.02591% | EFF Risk, CFO Other Risk
639 | BALCOM_RAR0085_RCS1211 | 3.2611 | 0.068903 | 0.068901 | 1.2e-05 | 0.02586% | EFF Risk, CFO Other Risk
640 | EVERETT_GS8593-2_EOL | 3.0597 | 0.068595 | 0.068594 | 3.73e-05 | 0.02574% | EFF Risk, CFO Other Risk
641 | BOULDER_RAR0240_GS1873-1 | 5.5343 | 0.06849 | 0.068488 | 6.18e-05 | 0.0257% | EFF Risk, CFO Other Risk
642 | UNDERWOOD_RCS0363_EOL | 5.0639 | 0.068454 | 0.068451 | 5.25e-06 | 0.02569% | EFF Risk, CFO Other Risk
643 | RAMSGATE_GS8135-2_EOL | 0.83435 | 0.068345 | 0.068345 | 1.89e-05 | 0.02565% | EFF Risk, CFO Other Risk
644 | CANEBRAKE_RAR0625_RAR0909 | 14.5299 | 0.068074 | 0.068071 | 1.27e-05 | 0.02555% | EFF Risk, CFO Other Risk
645 | POULTRY_RAR0024_RAR0182 | 5.7112 | 0.067913 | 0.06791 | 2.82e-05 | 0.02549% | EFF Risk, CFO Other Risk
646 | PAYNE_RAR0963_RAR0970 | 3.5866 | 0.067732 | 0.067729 | 3.49e-05 | 0.02542% | EFF Risk, CFO Other Risk
647 | TWIN PEAKS_CB_RCS0435 | 2.4521 | 0.06735 | 0.06735 | 0 | 0.02527% | EFF Risk, CFO Other Risk
648 | WARHAWK_PS0611_RSR0122 | 2.6625 | 0.067345 | 0.067343 | 2.06e-05 | 0.02527% | EFF Risk, CFO Other Risk
649 | CRESCENTA_CB_RCS0643 | 6.1803 | 0.067296 | 0.067289 | 7.73e-05 | 0.02525% | EFF Risk, CFO Other Risk
650 | ALPINE_CB_RAR0035_RAR0037_RAR0005 | 2.0465 | 0.067214 | 0.067213 | 1.31e-05 | 0.02522% | EFF Risk, CFO Other Risk
651 | STANWOOD_RCS0185_RAR0395 | 3.4189 | 0.067073 | 0.06707 | 2.55e-05 | 0.02517% | EFF Risk, CFO Other Risk
652 | WHIPSTOCK_RAR0351_EOL | 3.1792 | 0.067053 | 0.067053 | 1.36e-05 | 0.02516% | EFF Risk, CFO Other Risk
653 | JULIUS_CB_EOL | 6.2986 | 0.067018 | 0.067005 | 0.00012638 | 0.02515% | EFF Risk, CFO Other Risk
654 | STARGLOW_RAR7502_RCS0959_RAR7401_ | 1.2306 | 0.067004 | 0.067004 | 7.14e-06 | 0.02514% | CFO Other Risk, EFF Risk
655 | TEXFI_RCS5560_EOL | 1.7015 | 0.066731 | 0.06673 | 1.96e-05 | 0.02504% | EFF Risk, CFO Other Risk
656 | GUITAR_RCS0510_EOL | 1.8524 | 0.066483 | 0.066482 | 2.56e-06 | 0.02495% | EFF Risk, CFO Other Risk
657 | BARLEY FLATS_CB_EOL | 2.6444 | 0.066294 | 0.06629 | 2.65e-05 | 0.02488% | EFF Risk, CFO Other Risk
658 | MATILIJA_RAR0329_EOL | 8.4945 | 0.06625 | 0.066249 | 5.44e-05 | 0.02486% | EFF Risk, CFO Other Risk
659 | HORNTOAD_PS0161_EOL | 1.5716 | 0.066022 | 0.066022 | 8.99e-06 | 0.02478% | EFF Risk, CFO Other Risk
660 | CEDAR PINES_CB_RCS0799 | 2.5714 | 0.065982 | 0.06598 | 1.44e-05 | 0.02476% | EFF Risk, CFO VEG Risk
661 | ENERGY_RAR0821_RCS8085-2 | 0.60893 | 0.065923 | 0.065923 | 2.19e-06 | 0.02474% | CFO Other Risk, EFF Risk
662 | SPRAGUE_RAR1648_EOL | 11.3733 | 0.065913 | 0.065912 | 2.26e-05 | 0.02473% | EFF Risk, CFO Other Risk
663 | ARMOUR_CB_RCS7135 | 3.9444 | 0.065832 | 0.065829 | 2.44e-05 | 0.0247% | EFF Risk, CFO Other Risk
664 | REVERSE PEAK_CB_RAR0152 | 7.2431 | 0.065813 | 0.065804 | 1.78e-05 | 0.0247% | EFF Risk, CFO Other Risk
665 | LEMONADE_RCS0218_EOL | 5.2832 | 0.065715 | 0.065711 | 4.9e-05 | 0.02466% | EFF Risk, CFO Other Risk
666 | WHITEHORN_RAR1185_EOL | 2.7873 | 0.065597 | 0.065589 | 1.43e-05 | 0.02462% | EFF Risk, CFO Other Risk
667 | UNDERWOOD_RAR0201_PS0391_RAR0009_ | 3.6024 | 0.065134 | 0.06513 | 5.4e-06 | 0.02444% | EFF Risk, CFO Other Risk
668 | NORTHPARK_RAR0824_RAR0822 | 2.2654 | 0.065008 | 0.065006 | 2.77e-05 | 0.02439% | EFF Risk, CFO Other Risk
669 | METTLER_RCS1132_EOL | 5.0018 | 0.064881 | 0.064879 | 1.01e-05 | 0.02435% | CFO Other Risk, EFF Risk
670 | SEACLIFF_RAR0114_EOL | 8.1243 | 0.064855 | 0.064853 | 7.29e-05 | 0.02434% | EFF Risk, CFO Other Risk
671 | DOCTORS_RAR1176_EOL | 1.5004 | 0.064853 | 0.064852 | 2.44e-05 | 0.02434% | CFO Other Risk, EFF Risk
672 | DOCTORS_RAR1177_EOL | 1.6205 | 0.064731 | 0.064731 | 2.15e-05 | 0.02429% | CFO Other Risk, EFF Risk
673 | PETIT_RAR1452_EOL | 4.1525 | 0.064668 | 0.064666 | 4.4e-06 | 0.02427% | EFF Risk, CFO Other Risk
674 | MUSTANG_PS0614_PS0648_PS0615_ | 3.9536 | 0.064371 | 0.064369 | 4.86e-06 | 0.02416% | EFF Risk, CFO Other Risk
675 | TONTO_RAR1258_EOL | 1.0337 | 0.064104 | 0.064103 | 2.62e-06 | 0.02406% | EFF Risk, CFO Other Risk
676 | STANWOOD_RCS1565_EOL | 5.0654 | 0.063793 | 0.063785 | 4.06e-05 | 0.02394% | EFF Risk, CFO Other Risk
677 | GORGE_CB_RCS0545 [2] | 1.4266 | 0.063467 | 0.063466 | 1.12e-05 | 0.02382% | EFF Risk, CFO Other Risk
678 | VALLECITO_RCS9708_EOL | 5.9096 | 0.063082 | 0.063069 | 0.00012974 | 0.02367% | EFF Risk, CFO Other Risk
679 | DINELY_RAR6451_EOL | 3.5574 | 0.06306 | 0.063059 | 9.24e-07 | 0.02366% | CFO Other Risk, EFF Risk
680 | STONEWOOD_RAR0857_EOL | 2.598 | 0.063039 | 0.063037 | 5.58e-06 | 0.02366% | EFF Risk, CFO Other Risk
681 | QUINBY_CB_RCS0329 | 2.372 | 0.06262 | 0.062601 | 5.26e-05 | 0.0235% | CFO Other Risk, EFF Risk
682 | PALOMINO_CB_RCS2208 | 2.9698 | 0.062604 | 0.062604 | 4.27e-05 | 0.02349% | EFF Risk, CFO Other Risk
683 | HASKELL_RAR4203_EOL | 4.8694 | 0.06248 | 0.062478 | 0.00022013 | 0.02345% | EFF Risk, CFO Other Risk
684 | CRUMNER_CB_RAR0033_RSR5731_ | 1.8948 | 0.062345 | 0.06234 | 7.95e-06 | 0.0234% | CFO Other Risk, EFF Risk
685 | EL MIRADOR_RAR0268_EOL | 15.6996 | 0.062331 | 0.062331 | 5.35e-06 | 0.02339% | EFF Risk, CFO Other Risk
686 | MORITZ_RCS0375_EOL | 2.5212 | 0.06226 | 0.062255 | 3.68e-05 | 0.02336% | EFF Risk, CFO Other Risk
687 | ARMOUR_RCS7135_EOL | 2.3667 | 0.061975 | 0.061974 | 1.37e-05 | 0.02326% | EFF Risk, CFO Other Risk
688 | STATLER_RAR0195_EOL | 3.7598 | 0.061821 | 0.06182 | 6.53e-05 | 0.0232% | EFF Risk, CFO Other Risk
689 | VIENTO_RCS7584-1_RCS1726 | 1.3375 | 0.061754 | 0.061753 | 2.39e-06 | 0.02317% | CFO Other Risk, EFF Risk
690 | GILMAN_CB_EOL | 2.1017 | 0.061702 | 0.061702 | 8.58e-08 | 0.02315% | CFO Other Risk, EFF Risk
691 | ZONE_RAR2385_EOL | 2.9744 | 0.06169 | 0.061689 | 5e-06 | 0.02315% | EFF Risk, CFO Other Risk
692 | CEDAR GLEN_CB_RAR0390_RAR0267_ | 1.198 | 0.061669 | 0.061666 | 9.8e-06 | 0.02314% | EFF Risk, CFO Other Risk
693 | MUDDY_CB_RCS0855 | 3.7723 | 0.061518 | 0.061515 | 2.88e-05 | 0.02309% | EFF Risk, CFO Other Risk
694 | SEXTON_RAR7428_EOL | 2.1822 | 0.061425 | 0.061423 | 6.12e-05 | 0.02305% | EFF Risk, CFO Other Risk
695 | SOGGY_RAR8009_EOL | 2.6865 | 0.061348 | 0.061348 | 1.1e-05 | 0.02302% | CFO Other Risk, EFF Risk
696 | SAUNDERS_RAR0134_RCS1579_RCS0985_ | 2.4269 | 0.061165 | 0.061164 | 8.81e-06 | 0.02295% | EFF Risk, CFO Other Risk
697 | ORION_CB_GS2116-1 | 3.358 | 0.060855 | 0.060846 | 0.00018615 | 0.02284% | CFO Other Risk, EFF Risk
698 | SEYMOUR_RCS0430_EOL | 5.562 | 0.060686 | 0.060686 | 0 | 0.02277% | EFF Risk, CFO Other Risk
699 | MEMPHIS_CB_RAR0234_RCS0414_ | 5.2865 | 0.060481 | 0.06048 | 8.95e-05 | 0.0227% | CFO Other Risk, EFF Risk
700 | DARTMOUTH_RAR7488_RSR9279 | 1.7116 | 0.060464 | 0.060463 | 2.14e-05 | 0.02269% | EFF Risk, CFO Other Risk
701 | TREMAINE_RAR1601_EOL | 2.3435 | 0.060173 | 0.060172 | 7.06e-06 | 0.02258% | EFF Risk, CFO Other Risk
702 | GINGER_CB_RCS0101_RCS0159_ | 4.7952 | 0.060139 | 0.060138 | 9.3e-06 | 0.02257% | EFF Risk, CFO Other Risk
703 | DRILLER_CB_EOL | 4.3297 | 0.059923 | 0.059922 | 7.36e-05 | 0.02249% | EFF Risk, CFO Other Risk
704 | CALAMAR_RCS1601_EOL | 4.7912 | 0.059863 | 0.059863 | 8.06e-06 | 0.02246% | EFF Risk, CFO Other Risk
705 | CHUCK WAGON_RCS7388-1_EOL | 1.6853 | 0.059803 | 0.059801 | 4.7e-05 | 0.02244% | CFO Other Risk, EFF Risk
706 | TENNECO_RAR3835_RCS0732 | 9.0211 | 0.059661 | 0.059655 | 7e-05 | 0.02239% | EFF Risk, CFO Other Risk
707 | FLYING D_RCS0654_EOL | 4.3652 | 0.059642 | 0.059642 | 3.95e-06 | 0.02238% | CFO Other Risk, EFF Risk
708 | SHASTA_CB_RSR1133 | 4.4642 | 0.05947 | 0.059469 | 1.71e-05 | 0.02232% | EFF Risk, CFO Other Risk
709 | CALGROVE_RCS6552-3_EOL | 1.0131 | 0.059062 | 0.05906 | 7.99e-06 | 0.02216% | EFF Risk, CFO Other Risk
710 | BEAR VALLEY_CB_RAR0244_RAR0519_ | 4.0905 | 0.058987 | 0.058987 | 7.99e-07 | 0.02214% | EFF Risk, CFO Other Risk
711 | HOSS_RCS1770-4_EOL | 2.6731 | 0.058772 | 0.05877 | 0.00021815 | 0.02205% | EFF Risk, CFO Other Risk
712 | ARGONAUT_CB_GS7029-3 | 2.188 | 0.058763 | 0.058762 | 7.77e-05 | 0.02205% | EFF Risk, CFO Other Risk
713 | BIRCHIM_RAR0164_RCS0181_RAR0323_ | 12.7465 | 0.058681 | 0.058675 | 1.75e-05 | 0.02202% | EFF Risk, CFO Other Risk
714 | PICKLE MEADOWS_CB_RAR0156 | 8.0997 | 0.05868 | 0.058679 | 5.17e-06 | 0.02202% | EFF Risk, CFO Other Risk
715 | CORSAIR_RAR0269_EOL | 11.3027 | 0.058669 | 0.058668 | 6.77e-05 | 0.02202% | EFF Risk, CFO Other Risk
716 | RIDGE_CB_PS0714_RCS0713_ | 8.7335 | 0.058656 | 0.058652 | 7.86e-06 | 0.02201% | EFF Risk, CFO Other Risk
717 | THACHER_RAR0721_RAR3659 | 10.4066 | 0.058567 | 0.058564 | 1.78e-05 | 0.02198% | EFF Risk, CFO Other Risk
718 | CORSAIR_RAR1249_EOL | 2.5125 | 0.058291 | 0.058291 | 1.5e-05 | 0.02187% | EFF Risk, CFO Other Risk
719 | ELSTER_RAR3535_EOL | 12.4284 | 0.057657 | 0.057655 | 2.02e-05 | 0.02164% | EFF Risk, CFO Other Risk
720 | VANDERLIP_CB_EOL | 1.385 | 0.057489 | 0.057489 | 1.59e-07 | 0.02157% | EFF Risk, CFO Other Risk
721 | FLYING D_RAR0655_RCS0654 | 6.2701 | 0.057488 | 0.057488 | 5.61e-06 | 0.02157% | CFO Other Risk, EFF Risk
722 | MAIZE_RAR6531_EOL | 2.3683 | 0.057405 | 0.057405 | 3.43e-05 | 0.02154% | EFF Risk, CFO Other Risk
723 | MANDARIN_RAR4843_EOL | 2.2958 | 0.057392 | 0.057389 | 6.44e-05 | 0.02154% | CFO Other Risk, EFF Risk
724 | COVENTRY_CB_RAR1224_RAR1055_ | 0.87473 | 0.057204 | 0.057204 | 4.88e-06 | 0.02147% | EFF Risk, CFO Other Risk
725 | RUIZ_CB_EOL | 6.6881 | 0.057167 | 0.05716 | 4.65e-05 | 0.02145% | EFF Risk, CFO Other Risk
726 | CUDDEBACK_RAR1098_EOL | 2.4062 | 0.057144 | 0.057143 | 3.01e-06 | 0.02144% | CFO Other Risk, EFF Risk
727 | TUFA_CB_RAR0289 | 5.6962 | 0.05698 | 0.056979 | 3.85e-06 | 0.02138% | EFF Risk, CFO Other Risk
728 | ONBORD_RAR3750_EOL | 1.319 | 0.056765 | 0.056763 | 3.72e-05 | 0.0213% | EFF Risk, CFO Other Risk
729 | SAN NICHOLAS_CB_RCS0025 | 4.6041 | 0.056598 | 0.056591 | 0.00015642 | 0.02124% | EFF Risk, CFO Other Risk
730 | HAMMOCK_RAR1757_EOL | 1.1723 | 0.056435 | 0.056435 | 8.7e-08 | 0.02118% | EFF Risk, CFO Other Risk
731 | ACAPULCO_RAR0750_EOL | 4.14 | 0.056362 | 0.056362 | 5.98e-07 | 0.02115% | CFO Other Risk, EFF Risk
732 | RIDGE_RCS0713_EOL | 4.9437 | 0.056056 | 0.056054 | 4.48e-06 | 0.02104% | EFF Risk, CFO Other Risk
733 | BALCOM_RCS1211_PS1066 | 7.625 | 0.05602 | 0.056015 | 2.71e-05 | 0.02102% | CFO Other Risk, EFF Risk
734 | SHEFFIELD_RAR4095_EOL | 3.3261 | 0.056007 | 0.056004 | 1.15e-05 | 0.02102% | EFF Risk, CFO Other Risk
735 | GALAHAD_RCS0658_EOL | 4.8343 | 0.055876 | 0.055873 | 2.55e-05 | 0.02097% | EFF Risk, CFO Other Risk
736 | PORPHYRY_GS8705-1_EOL | 3.2093 | 0.055524 | 0.055524 | 3.47e-07 | 0.02084% | EFF Risk, CFO Other Risk
737 | BONANZA_PS0713_EOL | 4.649 | 0.055498 | 0.055496 | 9.27e-06 | 0.02083% | EFF Risk, CFO Other Risk
738 | HILLCREST_CB_RCS0107 | 8.1109 | 0.055427 | 0.055423 | 9.36e-05 | 0.0208% | EFF Risk, CFO Other Risk
739 | BOUQUET_BF59433_EOL | 1.1046 | 0.05515 | 0.05515 | 2.5e-06 | 0.0207% | EFF Risk, CFO Other Risk
740 | SPANADA_CB_RCS0379 | 2.6563 | 0.055146 | 0.055144 | 2.58e-06 | 0.02069% | CFO Other Risk, EFF Risk
741 | MONARCH_CB_EOL | 3.4129 | 0.055038 | 0.055028 | 7.45e-05 | 0.02065% | CFO Other Risk, EFF Risk
742 | HOOK CREEK_CB_EOL | 3.1737 | 0.054815 | 0.054811 | 3.1e-05 | 0.02057% | EFF Risk, CFO Other Risk
743 | CROFT_CB_RCS0764-2 | 1.7156 | 0.054711 | 0.054706 | 3.6e-05 | 0.02053% | EFF Risk, CFO Other Risk
744 | TIOGA_RAR0442_EOL | 3.2165 | 0.054675 | 0.054675 | 4.98e-06 | 0.02052% | EFF Risk, CFO Other Risk
745 | NERO_RCS0097_EOL | 5.4445 | 0.054262 | 0.054255 | 5.93e-05 | 0.02036% | EFF Risk, CFO Other Risk
746 | PALMER_RAR0302_EOL | 1.9821 | 0.054111 | 0.05411 | 4.12e-05 | 0.02031% | EFF Risk, CFO Other Risk
747 | CONESTOGA_CB_PS1934 | 3.2462 | 0.053855 | 0.053854 | 2.11e-05 | 0.02021% | EFF Risk, CFO Other Risk
748 | ATENTO_RAR3342_EOL | 2.608 | 0.053807 | 0.053805 | 2.46e-05 | 0.02019% | EFF Risk, CFO Other Risk
749 | SPRAGUE_RCS0138_RAR1648 | 13.1693 | 0.053709 | 0.053707 | 2.64e-05 | 0.02015% | EFF Risk, CFO Other Risk
750 | OMEGA_RAR0543_EOL | 2.0657 | 0.05357 | 0.05357 | 7.38e-06 | 0.0201% | CFO Other Risk, EFF Risk
751 | ACROBAT_CB_RCS3323 | 3.2916 | 0.053552 | 0.053544 | 2.87e-05 | 0.0201% | EFF Risk, CFO Other Risk
752 | TITAN_RAR0265_RCS5472_RCS0890_ | 7.0747 | 0.053442 | 0.05344 | 1.01e-05 | 0.02005% | EFF Risk, CFO Other Risk
753 | WHIP_PS1224_EOL | 2.7657 | 0.053338 | 0.05333 | 3.44e-05 | 0.02002% | CFO Other Risk, EFF Risk
754 | WILDOMAR_RAR0925_RCS1349 | 2.7667 | 0.053297 | 0.053297 | 5.95e-09 | 0.02% | CFO Other Risk, EFF Risk
755 | LAST_CB_EOL | 1.0937 | 0.053232 | 0.053232 | 6.14e-05 | 0.01998% | EFF Risk, CFO Other Risk
756 | GALAHAD_RAR0652_RAR3693 | 3.6651 | 0.053189 | 0.053188 | 1.9e-05 | 0.01996% | EFF Risk, CFO Other Risk
757 | ANGUS_RAR0130_RAR1505 | 8.6381 | 0.053028 | 0.053022 | 9.25e-05 | 0.0199% | EFF Risk, CFO Other Risk
758 | RHODA_RCS8860_EOL | 0.86868 | 0.052825 | 0.052824 | 7.03e-06 | 0.01982% | CFO Other Risk, EFF Risk
759 | JEEP_CB_RAR0355 | 6.4969 | 0.052698 | 0.05269 | 3.04e-05 | 0.01978% | EFF Risk, CFO Other Risk
760 | SAGEHEN_RSR0455_RAR0028_RAR0404_ | 6.0815 | 0.05252 | 0.052519 | 8.09e-06 | 0.01971% | EFF Risk, CFO Other Risk
761 | PYTHON_RCS7945-1_RAR0066_RAR0215_ | 1.1375 | 0.052461 | 0.05246 | 2.15e-06 | 0.01969% | CFO Other Risk, EFF Risk
762 | STATLER_PS0265_EOL | 10.1476 | 0.05239 | 0.052387 | 0.00017589 | 0.01966% | EFF Risk, CFO Other Risk
763 | FLANDERS_PD0606_EOL | 2.3002 | 0.052388 | 0.052387 | 3.44e-06 | 0.01966% | EFF Risk, CFO Other Risk
764 | FIREBIRD_RSR0552_RCS5485-1_RCS5429-3_RSR2175 | 1.5287 | 0.051894 | 0.051894 | 1.13e-05 | 0.01947% | CFO Other Risk, EFF Risk
765 | ANZAR_CB_EOL | 3.168 | 0.05187 | 0.05187 | 0 | 0.01946% | EFF Risk, CFO Other Risk
766 | BEAR VALLEY_RAR0244_RAR0537 | 3.2177 | 0.05186 | 0.05186 | 6.27e-07 | 0.01946% | EFF Risk, CFO Other Risk
767 | QUARRY_CB_RCS0370 | 3.567 | 0.051802 | 0.051798 | 2.52e-05 | 0.01944% | EFF Risk, CFO Other Risk
768 | SHASTA_RSR1133_EOL | 3.0017 | 0.051541 | 0.05154 | 1.17e-05 | 0.01934% | EFF Risk, CFO Other Risk
769 | TREMAINE_RAR1602_EOL | 0.82705 | 0.051474 | 0.051473 | 2.38e-06 | 0.01932% | EFF Risk, CFO Other Risk
770 | VERA CRUZ_RAR0870_EOL | 1.7823 | 0.051412 | 0.051411 | 3e-06 | 0.01929% | CFO Other Risk, EFF Risk
771 | ACRES_RCS0515-1_RCS0530 | 1.4212 | 0.051216 | 0.051215 | 4.69e-05 | 0.01922% | EFF Risk, CFO Other Risk
772 | TWIN LAKES_RCS0557_RCS0473 | 0.48064 | 0.051208 | 0.051202 | 3.43e-05 | 0.01922% | CFO Other Risk, EFF Risk
773 | CALIBER_RAR0980_PS0989_RAR0034_ | 1.5103 | 0.050579 | 0.050575 | 7.69e-06 | 0.01898% | CFO Other Risk, EFF Risk
774 | BALDWIN_RCS0007_EOL | 5.3795 | 0.050418 | 0.050416 | 7.66e-05 | 0.01892% | EFF Risk, CFO Other Risk
775 | VERA CRUZ_RAR7638_RCS6376 | 1.3084 | 0.050346 | 0.050345 | 2.18e-06 | 0.01889% | CFO Other Risk, EFF Risk
776 | HASS_CB_RAR0580_RAR0116_ | 3.4743 | 0.050261 | 0.05026 | 6.32e-05 | 0.01886% | EFF Risk, CFO Other Risk
777 | RIM_RAR0274_RCS0316 | 1.9239 | 0.050013 | 0.05001 | 2.62e-05 | 0.01877% | EFF Risk, CFO Other Risk
778 | TIN MINE_CB_RAR8902_RAR7265_RAR4801 | 4.2563 | 0.04982 | 0.04982 | 4.55e-05 | 0.0187% | CFO Other Risk, EFF Risk
779 | HIGH SCHOOL_RAR0043_EOL | 3.5734 | 0.049795 | 0.049792 | 6.67e-06 | 0.01869% | EFF Risk, CFO VEG Risk
780 | TOLL_RAR0216_EOL | 5.3153 | 0.049775 | 0.049774 | 1.21e-05 | 0.01868% | EFF Risk, CFO Other Risk
781 | SWEETWATER_CB_RCS1451-1 | 1.9395 | 0.049749 | 0.04972 | 7.5e-05 | 0.01867% | CFO Other Risk, EFF Risk
782 | MORITZ_RAR0652_RCS0363 | 1.7985 | 0.049727 | 0.049725 | 2.62e-05 | 0.01866% | EFF Risk, CFO VEG Risk
783 | TETLEY_RCS0668_RAR0871 | 4.5768 | 0.049616 | 0.049609 | 3.37e-05 | 0.01862% | EFF Risk, CFO Other Risk
784 | TATANKA_RCS0479_EOL | 1.3414 | 0.049253 | 0.049252 | 1.27e-06 | 0.01848% | EFF Risk, CFO Other Risk
785 | ARIEL_GS6979-1_EOL | 0.29911 | 0.049003 | 0.049003 | 3.46e-05 | 0.01839% | EFF Risk, CFO Other Risk
786 | NOVA_CB_PME6385-2_RCS1863-3_ | 3.0858 | 0.048855 | 0.048852 | 6.93e-05 | 0.01833% | EFF Risk, CFO Other Risk
787 | AUTUMN_RAR0301_EOL | 3.69 | 0.048815 | 0.0488 | 6.84e-05 | 0.01832% | EFF Risk, CFO Other Risk
788 | BUCKHORN_PS0553_EOL | 3.4883 | 0.048803 | 0.048802 | 8.36e-06 | 0.01831% | EFF Risk, CFO Other Risk
789 | MULHOLLAND_RAR0108_EOL | 2.8583 | 0.04877 | 0.048769 | 2.23e-06 | 0.0183% | EFF Risk, CFO Other Risk
790 | RIM_RCS0316_EOL | 2.9471 | 0.048749 | 0.048744 | 4.2e-05 | 0.01829% | EFF Risk, CFO Other Risk
791 | AUTUMN_CB_RAR0301 | 2.5454 | 0.048724 | 0.048712 | 4.81e-05 | 0.01828% | EFF Risk, CFO Other Risk
792 | CAMP ANGELUS_CB_EOL | 3.7014 | 0.048701 | 0.048696 | 3.36e-05 | 0.01828% | EFF Risk, CFO VEG Risk
793 | MOAB_CB_EOL | 0.51563 | 0.048601 | 0.048601 | 1.64e-06 | 0.01824% | EFF Risk, CFO Other Risk
794 | OWENS_RAR0392_RAR0037 | 1.4775 | 0.048486 | 0.048486 | 6.61e-07 | 0.01819% | EFF Risk, CFO Other Risk
795 | JARVIS_RAR0990_RAR0991 | 4.1638 | 0.04845 | 0.048449 | 1.05e-05 | 0.01818% | CFO Other Risk, EFF Risk
796 | ARCHIE_CB_RAR7232_RAR1340_ | 3.3127 | 0.048436 | 0.048436 | 2.21e-08 | 0.01818% | EFF Risk, CFO Other Risk
797 | RUBIN_RCS0030_EOL | 1.1626 | 0.048195 | 0.048194 | 1.86e-05 | 0.01809% | CFO Other Risk, EFF Risk
798 | SALT CREEK_CB_RAR0671_RAR1620_ | 9.8478 | 0.048108 | 0.048106 | 2.41e-05 | 0.01805% | EFF Risk, CFO Other Risk
799 | GUITAR_RCS0317_RAR0386 | 7.4288 | 0.048094 | 0.048093 | 1.02e-05 | 0.01805% | EFF Risk, CFO Other Risk
800 | FLYING D_CB_RAR0610_RAR0655_ | 6.6862 | 0.048014 | 0.048013 | 6.05e-06 | 0.01802% | CFO Other Risk, EFF Risk
801 | ACADIAN_RAR0157_EOL | 3.1038 | 0.047942 | 0.047941 | 6.56e-06 | 0.01799% | CFO Other Risk, EFF Risk
802 | TIN MINE_RAR8902_EOL | 4.2855 | 0.047872 | 0.047872 | 4.58e-05 | 0.01796% | EFF Risk, CFO Other Risk
803 | MORGANSTEIN_PS0471_GS0491-1 | 1.0974 | 0.047848 | 0.047848 | 1.45e-05 | 0.01796% | CFO Other Risk, EFF Risk
804 | CACHUMA_CB_RCS0244-1_RAR0078_P5030477-A | 3.8593 | 0.047722 | 0.047719 | 3.28e-05 | 0.01791% | CFO Other Risk, EFF Risk
805 | PALMER_RAR6205_EOL | 1.9043 | 0.04769 | 0.04769 | 3.41e-05 | 0.0179% | EFF Risk, CFO Other Risk
806 | EASTER_RAR7453_EOL | 3.882 | 0.047532 | 0.04753 | 2.36e-05 | 0.01784% | EFF Risk, CFO Other Risk
807 | CLARINET_RAR0627_RAR0297 | 3.3003 | 0.047395 | 0.047387 | 2.18e-05 | 0.01779% | EFF Risk, CFO Other Risk
808 | VALLECITO_RCS0299_RCS9708 | 2.9908 | 0.047066 | 0.047058 | 6.62e-05 | 0.01766% | EFF Risk, CFO Other Risk
809 | TEJON_CB_RAR2183_RAR0500_RCS1316 | 8.3592 | 0.047004 | 0.047 | 1.36e-05 | 0.01764% | CFO Other Risk, EFF Risk
810 | CHANTRY_RAR4178_EOL | 6.2833 | 0.046945 | 0.04694 | 0.00023076 | 0.01762% | EFF Risk, CFO Other Risk
811 | THACHER_CB_RSR9630_RAR5062_RAR0721_RSR0053__ | 6.368 | 0.046898 | 0.046897 | 1.11e-05 | 0.0176% | EFF Risk, CFO Other Risk
812 | ICE HOUSE_CB_EOL | 1.0542 | 0.046795 | 0.046795 | 1.64e-06 | 0.01756% | EFF Risk, CFO Other Risk
813 | DARTMOUTH_GS9046-2_RCS1093 | 2.0025 | 0.046757 | 0.046756 | 2.5e-05 | 0.01755% | CFO Other Risk, EFF Risk
814 | ROWCO_RCS0665_EOL | 2.919 | 0.046658 | 0.046654 | 7.54e-05 | 0.01751% | EFF Risk, CFO Other Risk
815 | TICO_RAR0246_EOL | 7.3911 | 0.046641 | 0.046638 | 3.37e-05 | 0.0175% | CFO Other Risk, EFF Risk
816 | ROBIN_CB_RCS0492 | 2.0086 | 0.046435 | 0.046435 | 1.18e-06 | 0.01743% | CFO Other Risk, EFF Risk
817 | PINE COVE_RCS0380_PS1668 | 3.0728 | 0.046434 | 0.046433 | 1.95e-05 | 0.01742% | CFO Other Risk, EFF Risk
818 | SHEFFIELD_CB_RAR4095_RAR0183_ | 6.0695 | 0.046224 | 0.046212 | 2.63e-05 | 0.01735% | EFF Risk, CFO Other Risk
819 | ANTON_PS1995_EOL | 3.4668 | 0.046051 | 0.046051 | 1.68e-06 | 0.01728% | EFF Risk, CFO Other Risk
820 | SANTORINI_RAR7198_EOL | 1.3903 | 0.046037 | 0.046036 | 1.26e-05 | 0.01728% | EFF Risk, CFO Other Risk
821 | HASS_RAR0580_EOL | 6.5871 | 0.046024 | 0.046021 | 0.00012072 | 0.01727% | EFF Risk, CFO Other Risk
822 | ATENTO_PS0673_PS0402 | 0.71359 | 0.045792 | 0.045792 | 6.74e-06 | 0.01718% | CFO Other Risk, EFF Risk
823 | BONNEVILLE_RAR7500_EOL | 2.3247 | 0.045775 | 0.045774 | 2.92e-06 | 0.01718% | EFF Risk, CFO Other Risk
824 | ANGUS_RCS5022-2_RAR0130 | 3.1033 | 0.045628 | 0.045625 | 3.36e-05 | 0.01712% | EFF Risk, CFO Other Risk
825 | MORELAND_RAR1389_EOL | 5.0601 | 0.045342 | 0.045334 | 7.03e-05 | 0.01701% | EFF Risk, CFO Other Risk
826 | QUICKSILVER_CB_RSR0177_RAR0324_ | 7.0775 | 0.045182 | 0.045179 | 6.64e-05 | 0.01696% | EFF Risk, CFO Other Risk
827 | LAZARO_CB_EOL | 0.67672 | 0.04509 | 0.04509 | 7.97e-05 | 0.01692% | EFF Risk, CFO Other Risk
828 | LA GRANDE_RCS0475_EOL | 0.92075 | 0.04504 | 0.045034 | 2.66e-05 | 0.0169% | CFO Other Risk, EFF Risk
829 | OLIVER_RAR7927_EOL | 8.7424 | 0.044976 | 0.044976 | 1.98e-07 | 0.01688% | EFF Risk, CFO Other Risk
830 | PENSTOCK_CB_EOL | 7.822 | 0.044921 | 0.044915 | 2.17e-05 | 0.01686% | CFO Other Risk, EFF Risk
831 | CAESAR_RCS0610_RCS7624-2 | 2.1255 | 0.044494 | 0.044489 | 7.01e-06 | 0.0167% | EFF Risk, CFO Other Risk
832 | ALPINE_RAR0035_EOL | 3.7495 | 0.044488 | 0.044486 | 2.39e-05 | 0.01669% | EFF Risk, CFO Other Risk
833 | PAYNE_RAR0962_EOL | 1.0421 | 0.044262 | 0.044262 | 9.09e-06 | 0.01661% | EFF Risk, CFO Other Risk
834 | ACADEMY_RCS0147_EOL | 6.641 | 0.044242 | 0.044241 | 2.54e-05 | 0.0166% | EFF Risk, CFO Other Risk
835 | CORSAIR_GS0032-1_RAR0179_RAR0268_RAR0269 | 4.5124 | 0.044142 | 0.044141 | 2.78e-05 | 0.01656% | EFF Risk, CFO Other Risk
836 | SILICONE_GS4002-2_RSR3079 | 7.8439 | 0.044115 | 0.044112 | 0.00029932 | 0.01655% | EFF Risk, CFO Other Risk
837 | BRENNAN_CB_RAR5082_PS0814_ | 1.7716 | 0.044008 | 0.044007 | 1.41e-05 | 0.01651% | CFO Other Risk, EFF Risk
838 | ENCANTO_PS0147_EOL | 2.1738 | 0.043915 | 0.043911 | 2.79e-05 | 0.01648% | EFF Risk, CFO Other Risk
839 | TONNER_RCS6192-5_EOL | 3.9604 | 0.043833 | 0.043831 | 5.42e-05 | 0.01645% | CFO Other Risk, EFF Risk
840 | POULTRY_RAR0668_RAR0024_PS0669_ | 2.5171 | 0.043741 | 0.04374 | 1.08e-05 | 0.01641% | EFF Risk, CFO Other Risk
841 | BRYDON_RAR0447_EOL | 4.184 | 0.043594 | 0.043591 | 0.00017696 | 0.01636% | CFO Other Risk, EFF Risk
842 | GUST_CB_RAR6457 | 5.9777 | 0.04345 | 0.043446 | 3.55e-05 | 0.01631% | EFF Risk, CFO Other Risk
843 | STUBBY_RCS0526_EOL | 6.4727 | 0.04344 | 0.04344 | 2.11e-07 | 0.0163% | EFF Risk, CFO Other Risk
844 | ANTON_RAR1992_EOL | 2.0661 | 0.043409 | 0.043409 | 9.85e-07 | 0.01629% | EFF Risk, CFO Other Risk
845 | THACHER_RAR1164_EOL | 8.9828 | 0.043408 | 0.043406 | 1.51e-05 | 0.01629% | EFF Risk, CFO Other Risk
846 | LA MANCHA_RAR0781_RCS4062 | 0.97859 | 0.043335 | 0.043335 | 1.3e-05 | 0.01626% | EFF Risk, CFO Other Risk
847 | CALIBER_CB_RCS0080_RAR0041_RAR0980 | 1.2296 | 0.043313 | 0.043311 | 4.4e-06 | 0.01625% | CFO Other Risk, EFF Risk
848 | SAUNDERS_RCS1579_EOL | 1.3883 | 0.0433 | 0.043299 | 5.04e-06 | 0.01625% | EFF Risk, CFO Other Risk
849 | STAGHORN_RSR0233_GS5793-2 | 1.169 | 0.043147 | 0.043145 | 1.24e-05 | 0.01619% | EFF Risk, CFO Other Risk
850 | TORONTO_RAR0535_EOL | 5.7681 | 0.043002 | 0.042996 | 5.54e-05 | 0.01614% | EFF Risk, CFO Other Risk
851 | THRUSH_CB_EOL | 4.6071 | 0.042893 | 0.042886 | 5.13e-05 | 0.0161% | EFF Risk, CFO Other Risk
852 | RAYBURN_CB_PS1245_RAR1638_PS2219 | 1.7243 | 0.042509 | 0.042506 | 1.58e-05 | 0.01595% | EFF Risk, CFO Other Risk
853 | TIMBER CANYON_RCS1254_EOL | 10.3964 | 0.042434 | 0.042432 | 1.49e-05 | 0.01592% | EFF Risk, CFO Other Risk
854 | LINNET_RAR1694_EOL | 2.4179 | 0.042345 | 0.042341 | 4.48e-05 | 0.01589% | EFF Risk, CFO Other Risk
855 | RESORT_RCS8919_RAR1461 | 0.96746 | 0.042263 | 0.042263 | 3.12e-08 | 0.01586% | CFO Other Risk, EFF Risk
856 | PINE COVE_RAR0218_RCS0069 | 5.213 | 0.04217 | 0.042168 | 3.31e-05 | 0.01582% | EFF Risk, CFO Other Risk
857 | ROBIN_RCS0492_RAR0495_BF73573_ | 1.6375 | 0.042138 | 0.042138 | 9.89e-07 | 0.01581% | EFF Risk, CFO Other Risk
858 | VERDEMONT_RCS1101_RAR0805 | 2.6366 | 0.041937 | 0.041937 | 1.45e-07 | 0.01574% | CFO Other Risk, EFF Risk
859 | GUITAR_RAR0041_EOL | 4.5408 | 0.041935 | 0.041934 | 6.26e-06 | 0.01574% | EFF Risk, CFO Other Risk
860 | OAK GLEN_RCS0059_EOL | 7.0072 | 0.041747 | 0.041744 | 2.28e-05 | 0.01567% | CFO Other Risk, EFF Risk
861 | BUFFER_RAR0801_RAR0330 | 0.2989 | 0.041734 | 0.041734 | 5.03e-06 | 0.01566% | CFO Other Risk, EFF Risk
862 | SAND CANYON_RCS6457-4_RAR3410 | 0.37436 | 0.041646 | 0.041645 | 1.93e-06 | 0.01563% | EFF Risk, CFO Other Risk
863 | TOWNSHIP_CB_EOL | 15.7901 | 0.041587 | 0.041572 | 0.00037624 | 0.01561% | EFF Risk, CFO Other Risk
864 | ATENTO_RCS3995-3_RAR7221_RAR7034_ | 0.36656 | 0.04153 | 0.04153 | 3.46e-06 | 0.01558% | CFO Other Risk, EFF Risk
865 | FLYING D_RAR0663_EOL | 4.2943 | 0.041216 | 0.041215 | 3.88e-06 | 0.01547% | EFF Risk, CFO Other Risk
866 | REVERSE PEAK_RAR0152_RAR0112 | 4.6176 | 0.041188 | 0.041183 | 1.05e-05 | 0.01546% | EFF Risk, CFO Other Risk
867 | RED BOX_CB_RAR1484 | 10.5951 | 0.041186 | 0.041185 | 1.34e-06 | 0.01546% | CFO Other Risk, EFF Risk
868 | OWENS_RAR0037_EOL | 2.2389 | 0.041117 | 0.041117 | 1e-06 | 0.01543% | EFF Risk, CFO Other Risk
869 | TRAUTWEIN_PS0071_RAR0306 | 2.5496 | 0.040634 | 0.040633 | 8.37e-06 | 0.01525% | EFF Risk, CFO Other Risk
870 | WHITECLIFF_CB_RCS5414-3_RCS5930-4_RCS5902 | 2.4632 | 0.040618 | 0.040612 | 3.81e-05 | 0.01524% | EFF Risk, CFO Other Risk
871 | ZENDA_RCS2147_EOL | 6.8965 | 0.040581 | 0.040581 | 3.15e-06 | 0.01523% | EFF Risk, CFO Other Risk
872 | STRIPER_CB_EOL | 1.0308 | 0.040572 | 0.040572 | 8.08e-10 | 0.01523% | EFF Risk, CFO Other Risk
873 | FAYE_RAR0675_EOL | 8.1559 | 0.0405 | 0.040497 | 1.99e-05 | 0.0152% | CFO Other Risk, EFF Risk
874 | HILLFIELD_RCS0471_RCS3816 | 1.0452 | 0.040472 | 0.04047 | 1.82e-05 | 0.01519% | EFF Risk, CFO Other Risk
875 | TAPO_RCS0701_RAR6509 | 2.223 | 0.040452 | 0.04045 | 5.53e-06 | 0.01518% | CFO Other Risk, EFF Risk
876 | MIST_RAR3857_RAR3862 | 14.6736 | 0.040241 | 0.040233 | 1.31e-05 | 0.0151% | EFF Risk, CFO Other Risk
877 | CUTHBERT_RCS5486_RCS0036_BF01510_RCS1692-1 | 0.75765 | 0.040212 | 0.040211 | 1.07e-05 | 0.01509% | EFF Risk, CFO Other Risk
878 | GOWAN_CB_EOL | 1.0359 | 0.040186 | 0.040182 | 3.72e-05 | 0.01508% | EFF Risk, CFO Other Risk
879 | PAINTED CAVE_CB_EOL | 1.9247 | 0.040123 | 0.040122 | 7.24e-06 | 0.01506% | EFF Risk, CFO Other Risk
880 | KUEHNER_RAR0454_EOL | 2.3864 | 0.039957 | 0.03995 | 9.45e-05 | 0.01499% | EFF Risk, CFO Other Risk
881 | TAVA_RAR1112_EOL | 1.8995 | 0.039879 | 0.039879 | 3.95e-06 | 0.01497% | EFF Risk, CFO Other Risk
882 | FIREBIRD_RCS5429-3_EOL | 0.87025 | 0.039855 | 0.039855 | 6.42e-06 | 0.01496% | CFO Other Risk, EFF Risk
883 | TANDEM_RCS1176_PS0121 | 8.8492 | 0.039707 | 0.039704 | 7.07e-05 | 0.0149% | EFF Risk, CFO Other Risk
884 | STATLER_CB_RAR0195_RAR0346_ | 6.6798 | 0.039521 | 0.039519 | 0.00011578 | 0.01483% | EFF Risk, CFO Other Risk
885 | PAWLEY_CB_RAR0551_RAR0804_RAR0451 | 9.8637 | 0.039442 | 0.039441 | 3.74e-05 | 0.0148% | CFO Other Risk, EFF Risk
886 | ESTABAN_CB_RAR7446_RAR9580_RCS2173 | 3.8393 | 0.039346 | 0.039341 | 3.61e-05 | 0.01477% | EFF Risk, CFO Other Risk
887 | ANGUS_RAR1505_EOL | 5.5692 | 0.039339 | 0.039335 | 5.86e-05 | 0.01476% | EFF Risk, CFO Other Risk
888 | RIVIERA_CB_EOL | 3.7458 | 0.039313 | 0.039309 | 2.16e-05 | 0.01475% | EFF Risk, CFO Other Risk
889 | ROUNDEL_CB_RCS2177-2 | 1.0519 | 0.038991 | 0.03899 | 2.3e-05 | 0.01463% | EFF Risk, CFO Other Risk
890 | SEELEY_RAR0046_EOL | 2.2651 | 0.038925 | 0.038921 | 1.4e-05 | 0.01461% | EFF Risk, CFO Other Risk
891 | BASIL_CB_PS1257 | 1.6964 | 0.038846 | 0.038845 | 1.51e-05 | 0.01458% | EFF Risk, CFO Other Risk
892 | KULBERG_CB_GS7577-1 | 1.5991 | 0.038769 | 0.038767 | 7.07e-05 | 0.01455% | EFF Risk, CFO Other Risk
893 | ATENTO_RSR6971_EOL | 3.5678 | 0.038752 | 0.038751 | 3.37e-05 | 0.01454% | EFF Risk, CFO Other Risk
894 | SOUTHRIDGE_CB_EOL | 0.41726 | 0.038649 | 0.038649 | 1.04e-06 | 0.0145% | EFF Risk, CFO Other Risk
895 | TERRA COTTA_CB_RAR1787 | 3.8718 | 0.038606 | 0.038606 | 1.62e-07 | 0.01449% | EFF Risk, CFO Other Risk
896 | MORITZ_RCS0363_EOL | 2.3994 | 0.038509 | 0.038505 | 3.51e-05 | 0.01445% | EFF Risk, CFO Other Risk
897 | HUGHES LAKE_RAR1495_RAR1546_RAR0442_ | 2.8783 | 0.038505 | 0.038503 | 3.78e-06 | 0.01445% | EFF Risk, CFO Other Risk
898 | DENTAL_RAR1090_RCS0327 | 1.6704 | 0.038428 | 0.038428 | 6.59e-06 | 0.01442% | CFO Other Risk, EFF Risk
899 | TWIN LAKES_RCS0473_EOL | 0.71888 | 0.038372 | 0.038367 | 4e-05 | 0.0144% | EFF Risk, CFO Other Risk
900 | VAL VERDE_CB_EOL | 2.6072 | 0.038326 | 0.038326 | 2.99e-06 | 0.01438% | CFO Other Risk, EFF Risk
901 | TRUMBLE_CB_EOL | 3.4827 | 0.038301 | 0.0383 | 1.46e-05 | 0.01437% | EFF Risk, CFO Other Risk
902 | CRUMNER_RAR0033_EOL | 2.8153 | 0.03825 | 0.038248 | 6.95e-06 | 0.01435% | EFF Risk, CFO Other Risk
903 | TREMAINE_CB_RAR1601_RAR1602_ | 1.814 | 0.038053 | 0.038052 | 5.64e-06 | 0.01428% | EFF Risk, CFO Other Risk
904 | WILSON CREEK_CB_RCS1657-1 | 3.8638 | 0.038009 | 0.038 | 3.72e-05 | 0.01426% | EFF Risk, CFO Other Risk
905 | SIMS_CB_EOL | 1.4834 | 0.037921 | 0.037912 | 3.16e-05 | 0.01423% | CFO Other Risk, EFF Risk
906 | BALCOM_PS1066_EOL | 3.6889 | 0.037763 | 0.037762 | 1.22e-05 | 0.01417% | EFF Risk, CFO Other Risk
907 | MILO_PS9711_RAR0210 | 3.5247 | 0.037738 | 0.037734 | 9.9e-05 | 0.01416% | EFF Risk, CFO Other Risk
908 | LAKELAND_CB_RAR7182 | 6.7637 | 0.037731 | 0.03773 | 1.85e-05 | 0.01416% | EFF Risk, CFO Other Risk
909 | LANGER_RAR0023_EOL | 6.9301 | 0.037628 | 0.037618 | 7.53e-05 | 0.01412% | EFF Risk, CFO Other Risk
910 | CRESTLINE_RAR1076_PS0711 | 0.96319 | 0.03759 | 0.037589 | 1.09e-05 | 0.01411% | EFF Risk, CFO VEG Risk
911 | BENCH_PS0916_EOL | 1.7262 | 0.03756 | 0.037559 | 4.16e-06 | 0.01409% | EFF Risk, CFO Other Risk
912 | BRUMFIELD_CB_GS5566-1 | 0.95942 | 0.037387 | 0.037387 | 1.42e-05 | 0.01403% | EFF Risk, CFO Other Risk
913 | JORDAN_RAR0847_EOL | 28.7241 | 0.037318 | 0.037317 | 1.5e-05 | 0.014% | EFF Risk, CFO Other Risk
914 | PINEWOOD_RCS2272_EOL | 0.93133 | 0.037278 | 0.037277 | 3.7e-06 | 0.01399% | EFF Risk, CFO Other Risk
915 | RIM_RAR0341_RCS0580 | 3.3316 | 0.037245 | 0.03724 | 4.4e-05 | 0.01398% | EFF Risk, CFO Other Risk
916 | ERSKINE_RAR0733_RAR0900_RCS0634_ | 1.6719 | 0.037161 | 0.03716 | 5.33e-06 | 0.01395% | CFO Other Risk, EFF Risk
917 | VALLECITO_RAR0353_RCS0299 | 3.9278 | 0.03714 | 0.037131 | 8.78e-05 | 0.01394% | EFF Risk, CFO Other Risk
918 | HARNAGE_RAR0618_EOL | 2.6484 | 0.037056 | 0.037056 | 1.02e-05 | 0.01391% | CFO Other Risk, EFF Risk
919 | BRAKEMAN_RCS0003_GS1805-2 | 5.6675 | 0.036986 | 0.036984 | 0.00011267 | 0.01388% | EFF Risk, CFO Other Risk
920 | SOGGY_CB_RAR8009 | 4.5252 | 0.036968 | 0.036966 | 1.91e-05 | 0.01387% | CFO Other Risk, EFF Risk
921 | CADWAY_RAR1280_EOL | 3.4803 | 0.036901 | 0.036896 | 5.92e-05 | 0.01385% | CFO Other Risk, EFF Risk
922 | ATLANTA_RCS6904-3_RAR0344 | 2.744 | 0.036822 | 0.036822 | 2.3e-05 | 0.01382% | EFF Risk, CFO Other Risk
923 | ZONE_PS2382_RAR0475 | 3.9329 | 0.036804 | 0.036803 | 6.76e-06 | 0.01381% | EFF Risk, CFO Other Risk
924 | WOBEGONE_RAR0738_RAR2322_RAR2321_ | 1.3321 | 0.036731 | 0.036731 | 8.81e-07 | 0.01378% | EFF Risk, CFO Other Risk
925 | ANTON_RCS0559_EOL | 4.7683 | 0.036723 | 0.036723 | 2.31e-06 | 0.01378% | CFO Other Risk, EFF Risk
926 | HOT SPRINGS_RCS1908-2_EOL | 1.8126 | 0.036646 | 0.036642 | 3.48e-05 | 0.01375% | EFF Risk, CFO Other Risk
927 | PATRICIA_RCS0283_RAR5140 | 4.4808 | 0.03661 | 0.036609 | 3.55e-05 | 0.01374% | EFF Risk, CFO Other Risk
928 | SINALOA_CB_RCS1593-1 | 4.2937 | 0.03658 | 0.036576 | 0.00022888 | 0.01373% | EFF Risk, CFO Other Risk
929 | NEAPOLITAN_RAR0610_EOL | 2.1907 | 0.036529 | 0.036528 | 6.01e-05 | 0.01371% | EFF Risk, CFO Other Risk
930 | GALAHAD_RCS0648_RAR0650 | 8.2963 | 0.036457 | 0.036453 | 4.32e-05 | 0.01368% | EFF Risk, CFO Other Risk
931 | LEVECHE_CB_PS0864 | 5.181 | 0.03644 | 0.036432 | 3.8e-05 | 0.01367% | EFF Risk, CFO Other Risk
932 | AVENIDA_RAR0233_EOL | 1.6999 | 0.036434 | 0.036432 | 5.2e-05 | 0.01367% | EFF Risk, CFO Other Risk
933 | STRATHERN_RAR5083_EOL | 1.7533 | 0.03642 | 0.036414 | 3.11e-05 | 0.01367% | EFF Risk, CFO Other Risk
934 | HUCKLEBERRY_RAR1384_1897858E | 2.0658 | 0.036404 | 0.036404 | 1.41e-06 | 0.01366% | CFO Other Risk, EFF Risk
935 | SUTT_RAR0818_EOL | 2.6693 | 0.036359 | 0.036356 | 2.42e-05 | 0.01364% | EFF Risk, CFO Other Risk
936 | DELUZ_RAR7803_EOL | 1.7493 | 0.036159 | 0.036159 | 4.81e-06 | 0.01357% | EFF Risk, CFO Other Risk
937 | TERRA COTTA_RAR1787_RCS8583 | 2.9288 | 0.03609 | 0.03609 | 1.22e-07 | 0.01354% | EFF Risk, CFO Other Risk
938 | CORONITA_PME3497-1_EOL | 0.41359 | 0.035903 | 0.035902 | 3.86e-05 | 0.01347% | EFF Risk, CFO Other Risk
939 | CRUMP_CB_RCS0638 | 2.8677 | 0.035877 | 0.035875 | 4.83e-05 | 0.01346% | EFF Risk, CFO Other Risk
940 | PAWLEY_RAR0551_EOL | 11.9621 | 0.035728 | 0.035726 | 4.52e-05 | 0.01341% | CFO Other Risk, EFF Risk
941 | CRESCENTA_RCS0622_EOL | 5.1206 | 0.035711 | 0.035703 | 6.24e-05 | 0.0134% | CFO Other Risk, EFF Risk
942 | KINNELOA_CB_PS0600 [2] | 2.3095 | 0.035671 | 0.035669 | 1.11e-05 | 0.01339% | EFF Risk, CFO Other Risk
943 | RAINBOW_RCS1736_BF39986 | 3.0602 | 0.035599 | 0.035599 | 3.58e-06 | 0.01336% | EFF Risk, CFO Other Risk
944 | SEXTON_RAR3032_EOL | 2.7429 | 0.035566 | 0.035564 | 7.79e-05 | 0.01335% | EFF Risk, CFO Other Risk
945 | CRAB_RCS0432_RCS0428 | 2.5367 | 0.035564 | 0.035564 | 1.08e-07 | 0.01335% | EFF Risk, CFO Other Risk
946 | LA SIERRA_CB_RCS0221 | 4.3911 | 0.035398 | 0.035398 | 1.81e-05 | 0.01328% | EFF Risk, CFO Other Risk
947 | COLLIER_CB_RAR0294 | 2.1372 | 0.035248 | 0.035247 | 1.67e-05 | 0.01323% | CFO Other Risk, EFF Risk
948 | MC ALLISTER_CB_EOL | 1.0021 | 0.035233 | 0.03523 | 7.48e-05 | 0.01322% | EFF Risk, CFO Other Risk
949 | CASE_CB_RCS1413 | 2.8404 | 0.035203 | 0.035203 | 2.26e-09 | 0.01321% | EFF Risk, CFO Other Risk
950 | DONNER_RAR8579_EOL | 1.8949 | 0.035155 | 0.035154 | 2.03e-05 | 0.01319% | CFO Other Risk, EFF Risk
951 | TENNECO_RAR0746_RAR0749 | 4.735 | 0.035096 | 0.035093 | 3.67e-05 | 0.01317% | EFF Risk, CFO Other Risk
952 | SNOW VALLEY_CB_RAR0610_RCS0560_ | 2.3691 | 0.035093 | 0.035087 | 4.86e-05 | 0.01317% | EFF Risk, CFO Other Risk
953 | ROBINSON CREEK_RAR0154_EOL | 8.5026 | 0.035078 | 0.035074 | 1.78e-05 | 0.01316% | EFF Risk, CFO Other Risk
954 | TOGA_CB_EOL | 3.0419 | 0.034933 | 0.034925 | 5.36e-05 | 0.01311% | EFF Risk, CFO Other Risk
955 | WESTFALL_RAR0565_EOL | 3.8155 | 0.034917 | 0.034914 | 1.62e-05 | 0.0131% | EFF Risk, CFO Other Risk
956 | OAK GLEN_CB_RAR0012 | 2.945 | 0.034802 | 0.034798 | 1.19e-05 | 0.01306% | CFO Other Risk, EFF Risk
957 | CRESTLINE_PS2041_EOL | 0.81182 | 0.034646 | 0.034645 | 9.17e-06 | 0.013% | EFF Risk, CFO Other Risk
958 | NAPOLEON_RCS0759-3_EOL | 0.56774 | 0.034639 | 0.034638 | 2.67e-05 | 0.013% | EFF Risk, CFO Other Risk
959 | WHIPSTOCK_RAR0030_EOL | 2.619 | 0.034631 | 0.034631 | 1.13e-05 | 0.013% | CFO Other Risk, EFF Risk
960 | ANTON_RAR0621_RAR1992_RCS0559_ | 4.3654 | 0.034585 | 0.034584 | 2.12e-06 | 0.01298% | EFF Risk, CFO Other Risk
961 | CUSHENBURY_RCS0506_EOL | 0.34469 | 0.034546 | 0.034546 | 2.89e-08 | 0.01296% | EFF Risk, CFO Other Risk
962 | HAMPSHIRE_CB_EOL | 19.7297 | 0.034522 | 0.034511 | 0.00016549 | 0.01295% | EFF Risk, CFO Other Risk
963 | ZENDA_RCS0310_EOL | 10.4937 | 0.034413 | 0.034412 | 4.72e-06 | 0.01291% | EFF Risk, CFO Other Risk
964 | BURNS_RSR1098_RCS2663-4 | 2.4499 | 0.034304 | 0.0343 | 3.16e-05 | 0.01287% | EFF Risk, CFO Other Risk
965 | ZONE_RCS2388_EOL | 5.0193 | 0.034146 | 0.034145 | 8.58e-06 | 0.01281% | EFF Risk, CFO Other Risk
966 | RHODA_CB_RCS8860 | 2.5719 | 0.03414 | 0.034137 | 2.09e-05 | 0.01281% | EFF Risk, CFO Other Risk
967 | MORITZ_RAR1218_EOL | 0.90937 | 0.034128 | 0.034126 | 2.04e-05 | 0.01281% | EFF Risk, CFO Other Risk
968 | HORIZON_RAR5174_PS0183 | 2.586 | 0.033983 | 0.033983 | 2.1e-05 | 0.01275% | EFF Risk, CFO Other Risk
969 | FELDSPAR_CB_RCS1055 | 4.1053 | 0.033666 | 0.033666 | 6.01e-05 | 0.01263% | EFF Risk, CFO Other Risk
970 | SKI_CB_EOL | 6.7304 | 0.033642 | 0.033642 | 0 | 0.01262% | EFF Risk, CFO Other Risk
971 | FLYNN_RAR2177_EOL | 2.8299 | 0.033633 | 0.033632 | 2.31e-05 | 0.01262% | EFF Risk, CFO Other Risk
972 | ROBIN_RAR0495_RCS0470 | 2.8699 | 0.033632 | 0.033631 | 1.74e-06 | 0.01262% | EFF Risk, CFO Other Risk
973 | BEAR VALLEY_RAR0537_RCS0806 | 5.2622 | 0.033624 | 0.033624 | 1.02e-06 | 0.01262% | EFF Risk, CFO Other Risk
974 | VALLEY OF THE MOON_CB_EOL | 6.3996 | 0.033616 | 0.03361 | 2.36e-05 | 0.01261% | EFF Risk, CFO VEG Risk
975 | OLIVER_RCS8501_EOL | 0.4126 | 0.033581 | 0.033581 | 1.37e-08 | 0.0126% | EFF Risk, CFO Other Risk
976 | BUCKHORN_CB_RCS1501 | 4.1453 | 0.033564 | 0.03356 | 1.44e-05 | 0.0126% | EFF Risk, CFO Other Risk
977 | VICASA_RAR5087_EOL [3] | 3.981 | 0.033535 | 0.033534 | 1.95e-05 | 0.01258% | EFF Risk, CFO Other Risk
978 | BABYLON_CB_EOL | 2.5221 | 0.033407 | 0.033406 | 3.12e-05 | 0.01254% | EFF Risk, CFO Other Risk
979 | LOCKNER_RAR1720_EOL | 1.1659 | 0.033346 | 0.033344 | 1.48e-05 | 0.01251% | EFF Risk, CFO Other Risk
980 | OMEGA_RAR0794_RAR0393_RAR0543_RAR0233 | 1.5637 | 0.033341 | 0.033341 | 5.94e-06 | 0.01251% | CFO Other Risk, EFF Risk
981 | GREAT SALT_RAR7499_EOL | 0.89638 | 0.033327 | 0.033327 | 3.64e-06 | 0.01251% | EFF Risk, CFO Other Risk
982 | CRAB_CB_RAR0051 | 2.08 | 0.033315 | 0.033315 | 9.55e-08 | 0.0125% | EFF Risk, CFO Other Risk
983 | URBITA_RCS0750_EOL | 1.8217 | 0.033247 | 0.033246 | 5.53e-06 | 0.01248% | EFF Risk, CFO Other Risk
984 | HASKELL_CB_RCS1897_RAR0517_ | 5.6112 | 0.033216 | 0.033213 | 0.00024942 | 0.01246% | EFF Risk, CFO Other Risk
985 | ROWCO_CB_RAR0041_RCS0665_ | 3.0152 | 0.033118 | 0.033113 | 7.89e-05 | 0.01243% | EFF Risk, CFO Other Risk
986 | SAVORY_RAR1058_RCS0094 | 3.5483 | 0.033027 | 0.033027 | 1.64e-06 | 0.01239% | EFF Risk, CFO Other Risk
987 | ESTABAN_RCS2173_EOL | 2.5166 | 0.03264 | 0.032638 | 2.35e-05 | 0.01225% | EFF Risk, CFO Other Risk
988 | BEELER_GS7588-1_RCS7242-3 | 2.9739 | 0.032529 | 0.032528 | 2.16e-05 | 0.01221% | EFF Risk, CFO Other Risk
989 | MIST_PS0013_EOL | 3.1293 | 0.032482 | 0.032481 | 1.95e-06 | 0.01219% | CFO Other Risk, EFF Risk
990 | SAGEHEN_RAR0028_EOL | 10.2471 | 0.032424 | 0.032422 | 1.25e-05 | 0.01217% | EFF Risk, CFO Other Risk
991 | NASHVILLE_CB_RCS1160-1 | 1.2936 | 0.032403 | 0.032401 | 1.63e-05 | 0.01216% | EFF Risk, CFO Other Risk
992 | EVITA_RAR1741_EOL | 3.4863 | 0.032365 | 0.032365 | 0.00011711 | 0.01215% | CFO Other Risk, EFF Risk
993 | CRABTREE_CB_GS1466-4_RCS4375-4_ | 3.5774 | 0.032338 | 0.032331 | 4.99e-05 | 0.01214% | EFF Risk, CFO Other Risk
994 | CRAM_RAR0814_EOL | 4.5015 | 0.03233 | 0.032328 | 3.92e-05 | 0.01213% | CFO Other Risk, EFF Risk
995 | CORINTH_CB_RCS1100 | 0.6959 | 0.032261 | 0.032261 | 1.23e-05 | 0.01211% | EFF Risk, CFO Other Risk
996 | SCALP_CB_EOL | 0.46467 | 0.032256 | 0.032256 | 6.56e-06 | 0.0121% | EFF Risk, CFO Other Risk
997 | STROSNIDER_RAR0058_EOL | 4.9467 | 0.032252 | 0.03225 | 2.3e-05 | 0.0121% | EFF Risk, CFO Other Risk
998 | DRINKWATER_CB_EOL | 1.8487 | 0.032232 | 0.032232 | 2.7e-07 | 0.0121% | EFF Risk, CFO Other Risk
999 | GLASSCOCK_RCS0624_EOL | 6.6898 | 0.032229 | 0.032223 | 6.57e-05 | 0.01209% | EFF Risk, CFO Other Risk
1000 | ZENDA_CB_RCS0310_RCS0309_ | 4.5108 | 0.032082 | 0.032081 | 2.04e-06 | 0.01204% | EFF Risk, CFO Other Risk
1001 | SABRINA_RAR0367_EOL | 2.121 | 0.032035 | 0.032035 | 2.39e-06 | 0.01202% | EFF Risk, CFO Other Risk
1002 | JERUSALEM_PME5694-3_EOL | 0.68085 | 0.031966 | 0.031965 | 5.25e-05 | 0.012% | EFF Risk, CFO Other Risk
1003 | LAUDA_RAR7056_EOL | 2.3819 | 0.031868 | 0.031868 | 1.13e-07 | 0.01196% | CFO Other Risk, EFF Risk
1004 | HURST_RCS0216_RAR0452_RAR0611_ | 4.1171 | 0.031848 | 0.031841 | 3.49e-05 | 0.01195% | EFF Risk, CFO Other Risk
1005 | TENDER_CB_EOL | 2.6606 | 0.031806 | 0.031797 | 1.51e-05 | 0.01194% | CFO Other Risk, EFF Risk
1006 | GUITAR_RAR0402_RCS0510 | 2.2958 | 0.031733 | 0.031733 | 3.17e-06 | 0.01191% | CFO Other Risk, EFF Risk
1007 | TUBA_RAR0225_RCS0333 [4] | 2.4612 | 0.031708 | 0.031705 | 4.86e-05 | 0.0119% | EFF Risk, CFO Other Risk
1008 | LINDERO_CB_GS0669-2 | 0.48455 | 0.0317 | 0.031683 | 4.48e-05 | 0.0119% | EFF Risk, CFO Other Risk
1009 | SHIRAZ_CB_EOL | 3.4623 | 0.031614 | 0.031609 | 3.98e-05 | 0.01186% | EFF Risk, CFO Other Risk
1010 | MORELLO_CB_RAR0450 | 1.9323 | 0.031512 | 0.031512 | 1.18e-06 | 0.01183% | EFF Risk, CFO Other Risk
1011 | VETERANS_RAR0117_PS0057_PS6666_ | 3.3271 | 0.031447 | 0.031442 | 1.91e-05 | 0.0118% | EFF Risk, CFO Other Risk
1012 | WESTBLUFF_CB_RAR0013 | 1.9664 | 0.031386 | 0.031385 | 7.1e-06 | 0.01178% | EFF Risk, CFO Other Risk
1013 | DREYER_RCS1528_EOL | 0.96772 | 0.031381 | 0.03138 | 3.52e-06 | 0.01178% | CFO Other Risk, EFF Risk
1014 | CLEMSON_CB_GS3887-3 | 2.3948 | 0.031363 | 0.031361 | 3.91e-05 | 0.01177% | EFF Risk, CFO Other Risk
1015 | ACE_CB_RAR0596 | 3.3702 | 0.031157 | 0.031153 | 2.95e-05 | 0.01169% | EFF Risk, CFO Other Risk
1016 | NORTH SHORE_RAR1121_RAR0339 | 3.7345 | 0.03105 | 0.03104 | 7.12e-05 | 0.01165% | EFF Risk, CFO Other Risk
1017 | INTERPACE_RCS0063_EOL | 4.2509 | 0.031042 | 0.031042 | 1.85e-07 | 0.01165% | EFF Risk, CFO Other Risk
1018 | BIDDER_RCS0303_EOL | 4.6113 | 0.030995 | 0.030994 | 1.43e-06 | 0.01163% | EFF Risk, CFO Other Risk
1019 | VERDUGO_CB_RCS1714-4 | 2.2136 | 0.030989 | 0.030984 | 1.51e-05 | 0.01163% | EFF Risk, CFO Other Risk
1020 | BIG FALLS_CB_EOL | 3.0082 | 0.030969 | 0.030968 | 5.95e-06 | 0.01162% | EFF Risk, CFO Other Risk
1021 | CASE_RCS1413_RCS6411-3 | 1.3271 | 0.030845 | 0.030845 | 9.34e-10 | 0.01158% | EFF Risk, CFO Other Risk
1022 | SUNDANCE_CB_GS5390-3 | 6.3137 | 0.030827 | 0.030826 | 3.39e-05 | 0.01157% | EFF Risk, CFO Other Risk
1023 | CRESTLINE_CB_RAR0021_RAR0708_ | 1.3155 | 0.030742 | 0.03074 | 1.62e-05 | 0.01154% | EFF Risk, CFO Other Risk
1024 | GOLDSMITH_CB_GS0518-3_RCS4028-1_ | 8.8459 | 0.030601 | 0.030573 | 0.00016183 | 0.01148% | EFF Risk, CFO Other Risk
1025 | RAINBOW_RAR1941_EOL | 3.4664 | 0.030591 | 0.030591 | 4.03e-06 | 0.01148% | EFF Risk, CFO Other Risk
1026 | STRATHERN_RCS0606_RSR0412 | 1.8613 | 0.030246 | 0.030239 | 3.34e-05 | 0.01135% | EFF Risk, CFO Other Risk
1027 | FIREBIRD_RCS2000_EOL | 2.5186 | 0.03024 | 0.03024 | 1.85e-05 | 0.01135% | EFF Risk, CFO Other Risk
1028 | TATANKA_RAR0461_RCS0479 | 1.2461 | 0.030066 | 0.030065 | 7.8e-07 | 0.01128% | EFF Risk, CFO VEG Risk
1029 | MONTREAL_PME0327-2_RAR0056 | 5.6817 | 0.030054 | 0.030047 | 5.01e-05 | 0.01128% | EFF Risk, CFO Other Risk
1030 | AMETHYST_RAR1239_EOL | 0.86387 | 0.030043 | 0.030039 | 3.68e-05 | 0.01127% | EFF Risk, CFO Other Risk
1031 | MORRIS_RAR9383_EOL | 4.4282 | 0.029843 | 0.029843 | 0.00011476 | 0.0112% | EFF Risk, CFO Other Risk
1032 | WIGWAG_CB_GS4833-1 | 0.52458 | 0.029838 | 0.029834 | 7.4e-05 | 0.0112% | EFF Risk, CFO Other Risk
1033 | PATRICIA_RAR0360_EOL | 11.4815 | 0.029835 | 0.029831 | 9.51e-05 | 0.0112% | EFF Risk, CFO Other Risk
1034 | TOMAHAWK_CB_RAR6465_RAR6459_ | 3.9774 | 0.029769 | 0.029763 | 2.81e-05 | 0.01117% | EFF Risk, CFO Other Risk
1035 | FLANDERS_CB_PD0606 | 2.3354 | 0.029698 | 0.029697 | 3.5e-06 | 0.01114% | EFF Risk, CFO Other Risk
1036 | TAPO_PS0046_EOL | 1.4826 | 0.02965 | 0.029648 | 3.69e-06 | 0.01113% | EFF Risk, CFO Other Risk
1037 | FANO_RAR0438_EOL | 1.684 | 0.029528 | 0.029528 | 9.47e-06 | 0.01108% | CFO Other Risk, EFF Risk
1038 | REDBALL_CB_GS5082-1 | 0.85544 | 0.029475 | 0.029474 | 5.46e-05 | 0.01106% | EFF Risk, CFO Other Risk
1039 | TENNECO_RCS0732_EOL | 8.2772 | 0.029241 | 0.029235 | 6.42e-05 | 0.01097% | EFF Risk, CFO Other Risk
1040 | BADGER_CB_GS4206-3 | 0.47037 | 0.029183 | 0.02918 | 2.2e-05 | 0.01095% | CFO Other Risk, EFF Risk
1041 | BENCH_CB_RSR1002 | 1.252 | 0.029116 | 0.029114 | 4.46e-06 | 0.01093% | EFF Risk, CFO Other Risk
1042 | SWIFT_RCS0462_EOL | 1.2971 | 0.029109 | 0.029108 | 3.18e-06 | 0.01092% | EFF Risk, CFO Other Risk
1043 | BOLLERO_RCS0275_EOL | 0.82927 | 0.029019 | 0.029018 | 3.24e-05 | 0.01089% | CFO Other Risk, EFF Risk
1044 | ROBIN_RCS0470_RCS1249 | 1.4523 | 0.028993 | 0.028992 | 8.51e-07 | 0.01088% | EFF Risk, CFO Other Risk
1045 | SABRINA_RAR0368_EOL | 2.2347 | 0.028982 | 0.028982 | 2.52e-06 | 0.01088% | EFF Risk, CFO Other Risk
1046 | STONEWOOD_CB_GS1156-2 | 1.0372 | 0.028916 | 0.028914 | 3.65e-06 | 0.01085% | EFF Risk, CFO Other Risk
1047 | EQUINOX_RAR7356_EOL | 14.374 | 0.028843 | 0.028842 | 1.67e-05 | 0.01082% | EFF Risk, CFO Other Risk
1048 | MORITZ_RAR1064_EOL | 4.5822 | 0.0288 | 0.028792 | 6.67e-05 | 0.01081% | EFF Risk, CFO Other Risk
1049 | SINKER_CB_EOL | 1.2985 | 0.028746 | 0.028746 | 6.98e-07 | 0.01079% | EFF Risk, CFO Other Risk
1050 | GUINNESS_RCS5085-5_EOL | 0.4072 | 0.028685 | 0.028684 | 9.66e-06 | 0.01076% | EFF Risk, CFO Other Risk
1051 | ROCKHILL_RAR7833_EOL | 4.3447 | 0.028569 | 0.028568 | 9.02e-06 | 0.01072% | CFO Other Risk, EFF Risk
1052 | ELSTER_CB_RSR0637_RAR3535_ | 12.1048 | 0.028361 | 0.02836 | 1.88e-05 | 0.01064% | EFF Risk, CFO Other Risk
1053 | TICO_PS0048_RAR0246 | 3.1408 | 0.028305 | 0.028304 | 1.42e-05 | 0.01062% | EFF Risk, CFO Other Risk
1054 | SNOWDRIFT_CB_EOL | 1.8195 | 0.0283 | 0.028284 | 4.02e-05 | 0.01062% | EFF Risk, CFO Other Risk
1055 | ELSTER_RAR0577_EOL | 13.0785 | 0.028281 | 0.028281 | 2.01e-05 | 0.01061% | EFF Risk, CFO Other Risk
1056 | BIRCHIM_RCS0181_RAR0223 | 5.6017 | 0.028223 | 0.02822 | 8.91e-06 | 0.01059% | EFF Risk, CFO Other Risk
1057 | MORGANSTEIN_GS0491-1_EOL | 0.47147 | 0.028159 | 0.028159 | 6.44e-06 | 0.01057% | EFF Risk, CFO Other Risk
1058 | APPALOUSA_RAR7506_EOL | 3.9649 | 0.028088 | 0.028085 | 2.32e-05 | 0.01054% | EFF Risk, CFO Other Risk
1059 | WHIZZIN_CB_EOL | 1.9237 | 0.028074 | 0.028069 | 2.48e-05 | 0.01054% | EFF Risk, CFO Other Risk
1060 | KERRY_CB_EOL | 3.6334 | 0.02807 | 0.028068 | 3.63e-05 | 0.01053% | EFF Risk, CFO Other Risk
1061 | EBERT_RCS2489-4_EOL | 1.2211 | 0.027966 | 0.027964 | 1.73e-05 | 0.01049% | EFF Risk, CFO Other Risk
1062 | RANIER_RSR1124_EOL | 0.76088 | 0.027943 | 0.027942 | 1.57e-05 | 0.01049% | EFF Risk, CFO Other Risk
1063 | ROSEMONT_CB_RCS0623 | 4.5404 | 0.027851 | 0.027848 | 1.58e-05 | 0.01045% | EFF Risk, CFO Other Risk
1064 | TUNA_GS1294-3_EOL | 1.674 | 0.027808 | 0.027808 | 1.87e-05 | 0.01044% | EFF Risk, CFO Other Risk
1065 | MIST_RAR3862_EOL | 8.6038 | 0.027495 | 0.027492 | 5.86e-06 | 0.01032% | EFF Risk, CFO Other Risk
1066 | ONAGA_RCS0431_RAR0853 | 1.3942 | 0.027472 | 0.027469 | 3.21e-06 | 0.01031% | EFF Risk, CFO Other Risk
1067 | LURING_CB_EOL | 2.5963 | 0.027448 | 0.027444 | 9.67e-05 | 0.0103% | EFF Risk, CFO Other Risk
1068 | TETLEY_CB_RCS0667 | 2.0116 | 0.027429 | 0.027426 | 1.46e-05 | 0.01029% | EFF Risk, CFO Other Risk
1069 | HELICOPTER_CB_PME2451-1 | 4.6303 | 0.027274 | 0.027271 | 2.2e-05 | 0.01024% | EFF Risk, CFO Other Risk
1070 | TUBA_CB_RAR0225 | 1.3194 | 0.02724 | 0.027238 | 2.56e-05 | 0.01022% | EFF Risk, CFO Other Risk
1071 | SAND CANYON_GS4326-3_RAR0238_GS8804-3_ | 1.8902 | 0.027132 | 0.02713 | 9.72e-06 | 0.01018% | EFF Risk, CFO Other Risk
1072 | ANTON_RAR1993_PS1995 | 0.99943 | 0.027072 | 0.027072 | 4.85e-07 | 0.01016% | EFF Risk, CFO Other Risk
1073 | RANIER_CB_GS1714-3_RSR1124_ | 0.93767 | 0.027036 | 0.027033 | 2.07e-05 | 0.01015% | EFF Risk, CFO Other Risk
1074 | TEJON_PS0529_EOL | 4.098 | 0.027023 | 0.027022 | 6.38e-06 | 0.01014% | CFO Other Risk, EFF Risk
1075 | LOPEZ_RAR0048_RAR3825 | 1.4115 | 0.027017 | 0.027016 | 4.74e-06 | 0.01014% | EFF Risk, CFO Other Risk
1076 | SHAKE_PS0419_EOL | 1.2119 | 0.026987 | 0.026987 | 0 | 0.01013% | EFF Risk, CFO Other Risk
1077 | TAGGERT_CB_RAR0499 | 1.9874 | 0.026977 | 0.026975 | 2.53e-05 | 0.01012% | EFF Risk, CFO Other Risk
1078 | SEACLIFF_RCS0751_RAR0114_RAR1653_ | 12.3738 | 0.026975 | 0.026971 | 0.00011183 | 0.01012% | EFF Risk, CFO Other Risk
1079 | BENCH_RSR1002_RAR0268 | 1.7456 | 0.026895 | 0.026895 | 4.29e-06 | 0.01009% | EFF Risk, CFO Other Risk
1080 | DYSART_RCS0290_EOL | 2.4159 | 0.026601 | 0.026601 | 3.51e-07 | 0.00998% | CFO Other Risk, EFF Risk
1081 | OAK GLEN_RAR0270_RCS0059 | 2.64 | 0.026417 | 0.026415 | 8.51e-06 | 0.00991% | EFF Risk, CFO Other Risk
1082 | DUKE_RAR0534_EOL | 2.1354 | 0.026204 | 0.026202 | 1.98e-05 | 0.00983% | EFF Risk, CFO Other Risk
1083 | NAPA_RAR7528_EOL | 4.3377 | 0.026178 | 0.026178 | 2.17e-05 | 0.00982% | EFF Risk, CFO Other Risk
1084 | SEELEY_CB_RAR0046_RAR1081_ | 2.0684 | 0.026114 | 0.026111 | 1.07e-05 | 0.0098% | EFF Risk, CFO Other Risk
1085 | SUCCESS_CB_RAR0491 | 2.988 | 0.026052 | 0.026049 | 1.73e-05 | 0.00978% | EFF Risk, CFO Other Risk
1086 | SKYLAND_CB_RAR0882 | 3.8888 | 0.025995 | 0.02599 | 2.41e-05 | 0.00975% | EFF Risk, CFO Other Risk
1087 | BLUE RIDGE_CB_EOL | 2.3894 | 0.025911 | 0.025911 | 1.57e-06 | 0.00972% | EFF Risk, CFO Other Risk
1088 | JORDAN_RAR0099_EOL | 28.2287 | 0.025878 | 0.025877 | 1.48e-05 | 0.00971% | EFF Risk, CFO Other Risk
1089 | LEON_GS6341-4_EOL | 0.73768 | 0.025869 | 0.025868 | 6.8e-05 | 0.00971% | EFF Risk, CFO Other Risk
1090 | CAMPANULA_RAR1058_EOL | 0.32667 | 0.025862 | 0.025859 | 1.43e-05 | 0.00971% | EFF Risk, CFO Other Risk
1091 | CACHUMA_PS0474_EOL | 3.1833 | 0.025843 | 0.02584 | 2.67e-05 | 0.0097% | EFF Risk, CFO Other Risk
1092 | POTTERY_RCS0654_EOL | 4.2975 | 0.025828 | 0.025827 | 1.79e-05 | 0.00969% | EFF Risk, CFO Other Risk
1093 | CHALON_CB_EOL | 0.86189 | 0.025794 | 0.025794 | 3.29e-08 | 0.00968% | EFF Risk, CFO Other Risk
1094 | ARBORETUM_CB_RAR0955 | 5.09 | 0.025759 | 0.025756 | 2.77e-05 | 0.00967% | EFF Risk, CFO Other Risk
1095 | SIENNA_RCS0121-3_EOL | 2.149 | 0.025737 | 0.025736 | 7.93e-06 | 0.00966% | EFF Risk, CFO Other Risk
1096 | ZONE_PS2386_RCS2388 | 7.1553 | 0.025631 | 0.025629 | 1.22e-05 | 0.00962% | EFF Risk, CFO Other Risk
1097 | WAHOO_RCS4259_EOL | 2.434 | 0.025625 | 0.02562 | 2.05e-05 | 0.00962% | EFF Risk, CFO Other Risk
1098 | ERRINGER_CB_EOL | 11.0931 | 0.025598 | 0.025582 | 0.00023403 | 0.00961% | EFF Risk, CFO Other Risk
1099 | PAWLEY_RAR0804_EOL | 17.9989 | 0.025565 | 0.025563 | 6.75e-05 | 0.00959% | EFF Risk, CFO Other Risk
1100 | AVIATOR_CB_RAR0534 | 4.0488 | 0.025451 | 0.02545 | 2.43e-05 | 0.00955% | EFF Risk, CFO Other Risk
1101 | BALDWIN_RCS0174_RCS0007 [2] | 6.4087 | 0.025344 | 0.025338 | 9.53e-05 | 0.00951% | CFO Other Risk, EFF Risk
1102 | PLATEAU_RAR1173_RCS3892-4 | 1.9402 | 0.025304 | 0.025303 | 1.57e-05 | 0.0095% | EFF Risk, CFO Other Risk
1103 | STUTZ_CB_RCS0396 | 3.7429 | 0.025271 | 0.025267 | 7.8e-05 | 0.00948% | CFO Other Risk, EFF Risk
1104 | SKYLAND_RAR0775_EOL | 1.9529 | 0.025267 | 0.025265 | 1.21e-05 | 0.00948% | EFF Risk, CFO Other Risk
1105 | PRESTON_PS1154_GS1468-4 | 1.0711 | 0.025251 | 0.025249 | 1.19e-05 | 0.00948% | CFO Other Risk, EFF Risk
1106 | ARABIA_RSR1212_EOL | 1.166 | 0.025231 | 0.025228 | 2.21e-05 | 0.00947% | EFF Risk, CFO Other Risk
1107 | PEAR_CB_GS0966-1 | 1.6077 | 0.025202 | 0.025201 | 3.03e-05 | 0.00946% | CFO Other Risk, EFF Risk
1108 | SPANADA_RCS0379_EOL | 1.8095 | 0.025168 | 0.025166 | 2.92e-06 | 0.00944% | CFO Other Risk, EFF Risk
1109 | COLT_CB_PME7659-1 | 0.76925 | 0.024984 | 0.024983 | 2.61e-05 | 0.00938% | EFF Risk, CFO Other Risk
1110 | MODJESKA_RAR0514_EOL | 1.1404 | 0.024979 | 0.024979 | 8.65e-05 | 0.00937% | EFF Risk, CFO Other Risk
1111 | PEARCE_CB_EOL | 2.711 | 0.024853 | 0.024851 | 1.17e-05 | 0.00933% | EFF Risk, CFO Other Risk
1112 | CHUMASH_CB_RCS4091-1 | 0.35914 | 0.024824 | 0.024824 | 4.46e-06 | 0.00932% | EFF Risk, CFO Other Risk
1113 | DALBA_CB_RAR0014_RAR0016_RAR0032 | 1.5992 | 0.024757 | 0.024755 | 3.41e-05 | 0.00929% | EFF Risk, CFO Other Risk
1114 | ENCHANTED_RCS5778-4_EOL | 0.27794 | 0.024654 | 0.024653 | 6.65e-07 | 0.00925% | CFO Other Risk, EFF Risk
1115 | LAWMAN_RSR6128_EOL | 3.2872 | 0.024626 | 0.024621 | 2.84e-05 | 0.00924% | EFF Risk, CFO Other Risk
1116 | MONTREAL_RAR0056_EOL | 6.1495 | 0.024308 | 0.024301 | 5.4e-05 | 0.00912% | EFF Risk, CFO Other Risk
1117 | RIM_RCS0580_RCS0306 | 4.3177 | 0.024198 | 0.024192 | 5.76e-05 | 0.00908% | EFF Risk, CFO Other Risk
1118 | TAPO_RCS5511-4_RCS0701 | 2.6292 | 0.024125 | 0.024122 | 6.55e-06 | 0.00905% | EFF Risk, CFO Other Risk
1119 | MCBEAN_RCS0126_EOL | 4.0222 | 0.024055 | 0.024051 | 8.74e-05 | 0.00903% | EFF Risk, CFO Other Risk
1120 | SUCCESS_RAR3691_EOL | 11.8955 | 0.02398 | 0.023978 | 6.05e-05 | 0.009% | EFF Risk, CFO Other Risk
1121 | KANAN_CB_GS0664-1 | 0.47542 | 0.023931 | 0.023902 | 0.00012475 | 0.00898% | EFF Risk, CFO Other Risk
1122 | PHEASANT_RAR2946_EOL | 1.1549 | 0.023836 | 0.023836 | 2.46e-06 | 0.00894% | EFF Risk, CFO Other Risk
1123 | LOWELL_RAR0980_EOL [2] | 2.4163 | 0.023773 | 0.023771 | 2.08e-05 | 0.00892% | CFO Other Risk, EFF Risk
1124 | SPIKE_CB_PME5105-2 | 0.68001 | 0.023689 | 0.023687 | 1.24e-05 | 0.00889% | EFF Risk, CFO Other Risk
1125 | SEACLIFF_RAR1653_EOL | 9.4515 | 0.023516 | 0.023514 | 8.42e-05 | 0.00882% | EFF Risk, CFO Other Risk
1126 | MIST_RAR9675_PS0013 | 2.219 | 0.023485 | 0.023482 | 3.05e-06 | 0.00881% | EFF Risk, CFO Other Risk
1127 | CHAMPION_PME4494-4_EOL | 0.34892 | 0.023401 | 0.023401 | 7.84e-05 | 0.00878% | EFF Risk, CFO Other Risk
1128 | SHETLAND_CB_PME5221-4 | 0.91799 | 0.023379 | 0.023379 | 1.03e-05 | 0.00877% | EFF Risk, CFO Other Risk
1129 | SIAM_RCS0887-3_EOL | 1.1919 | 0.023281 | 0.02328 | 5.03e-05 | 0.00874% | EFF Risk, CFO Other Risk
1130 | WAITE_CB_PME2579-1 | 3.0467 | 0.023233 | 0.02323 | 1.93e-05 | 0.00872% | EFF Risk, CFO Other Risk
1131 | SADDLEBACK_RCS1333_EOL | 2.4257 | 0.023154 | 0.023154 | 5.16e-08 | 0.00869% | CFO Other Risk, EFF Risk
1132 | PALOMINO_RCS2208_EOL | 2.0108 | 0.02314 | 0.02314 | 2.81e-05 | 0.00868% | CFO Other Risk, EFF Risk
1133 | FARMINGTON_RAR7452_EOL | 4.0098 | 0.023102 | 0.023101 | 2.8e-05 | 0.00867% | EFF Risk, CFO Other Risk
1134 | VIDEO_RAR1716_EOL [2] | 3.6753 | 0.023001 | 0.022999 | 1.63e-05 | 0.00863% | EFF Risk, CFO Other Risk
1135 | CUYAMA_RAR0770_EOL | 17.7246 | 0.022956 | 0.022955 | 3.92e-06 | 0.00861% | EFF Risk, CFO Other Risk
1136 | ANTON_RAR0217_RAR1993_RSR5773_ | 5.4114 | 0.022845 | 0.022844 | 2.62e-06 | 0.00857% | EFF Risk, CFO Other Risk
1137 | SANTORINI_RAR7192_EOL | 0.93567 | 0.022811 | 0.022811 | 8.43e-06 | 0.00856% | CFO Other Risk, EFF Risk
1138 | OVERLOOK_CB_EOL | 2.3113 | 0.022733 | 0.022732 | 7.48e-06 | 0.00853% | EFF Risk, CFO Other Risk
1139 | SPINKS_CB_EOL | 1.4145 | 0.022701 | 0.022699 | 5.35e-06 | 0.00852% | EFF Risk, CFO Other Risk
1140 | SKY HI_RAR1323_EOL | 3.5723 | 0.022673 | 0.022671 | 2.95e-05 | 0.00851% | EFF Risk, CFO Other Risk
1141 | DARTMOUTH_CB_GS9046-2 | 2.3897 | 0.022649 | 0.022648 | 2.93e-05 | 0.0085% | EFF Risk, CFO Other Risk
1142 | HEAPS PEAK_RCS0408_RCS0434 | 2.5148 | 0.022587 | 0.022587 | 1.09e-07 | 0.00848% | EFF Risk, CFO Other Risk
1143 | DALBA_RAR0014_EOL | 2.4943 | 0.022572 | 0.02257 | 5.14e-05 | 0.00847% | EFF Risk, CFO Other Risk
1144 | CHARIOT_GS6783-3_EOL | 1.5807 | 0.022547 | 0.022533 | 0.00014328 | 0.00846% | EFF Risk, CFO Other Risk
1145 | CONINE_RSR1128_RSR0661 | 0.7634 | 0.022539 | 0.022537 | 1.11e-05 | 0.00846% | EFF Risk, CFO Other Risk
1146 | DYNAMO_RAR0225_EOL | 10.1464 | 0.022458 | 0.022458 | 3.49e-07 | 0.00843% | EFF Risk, CFO Other Risk
1147 | ROMERO_RAR9229_EOL | 0.80477 | 0.022454 | 0.022454 | 1.67e-05 | 0.00843% | EFF Risk, CFO Other Risk
1148 | TOMAHAWK_RAR6465_EOL | 1.3284 | 0.022259 | 0.022256 | 1.01e-05 | 0.00835% | EFF Risk, CFO Other Risk
1149 | DEALER_PS0478_EOL | 1.7171 | 0.022217 | 0.022216 | 1.35e-05 | 0.00834% | CFO Other Risk, EFF Risk
1150 | KILKENNY_RAR1258_EOL | 4.0298 | 0.022101 | 0.022101 | 2.66e-05 | 0.00829% | CFO Other Risk, EFF Risk
1151 | BRAKEMAN_CB_RCS0003_RCS2891-2_ | 1.5731 | 0.022084 | 0.022083 | 3.15e-05 | 0.00829% | EFF Risk, CFO Other Risk
1152 | PENDLETON_CB_PS0391 | 0.87174 | 0.0219 | 0.021897 | 9.45e-06 | 0.00822% | EFF Risk, CFO Other Risk
1153 | BRYN MAWR_RAR0352_EOL | 1.4355 | 0.021855 | 0.021854 | 2.24e-05 | 0.0082% | EFF Risk, CFO Other Risk
1154 | BUCKBOARD_CB_EOL | 1.0268 | 0.021819 | 0.021819 | 1.31e-05 | 0.00819% | EFF Risk, CFO Other Risk
1155 | PUFF_CB_RCS7577 | 4.3792 | 0.021807 | 0.021806 | 1.59e-06 | 0.00818% | EFF Risk, CFO Other Risk
1156 | PALMER_CB_RAR0302_RAR6205_ | 1.5199 | 0.021758 | 0.021756 | 2.85e-05 | 0.00816% | EFF Risk, CFO Other Risk
1157 | RANKIN_PS0909_RAR0722 | 2.2043 | 0.021738 | 0.021738 | 8.49e-07 | 0.00816% | CFO Other Risk, EFF Risk
1158 | SURREY_CB_EOL | 1.5223 | 0.021727 | 0.021727 | 5.39e-06 | 0.00815% | EFF Risk, CFO VEG Risk
1159 | YOSEMITE_RCS5781-1_EOL | 0.44811 | 0.021689 | 0.021687 | 6.14e-06 | 0.00814% | EFF Risk, CFO Other Risk
1160 | EASTER_RCS6480-3_RAR7453 | 0.54262 | 0.021617 | 0.021616 | 2.82e-06 | 0.00811% | CFO Other Risk, EFF Risk
1161 | KUEHNER_CB_RAR0454 | 2.4711 | 0.021515 | 0.021509 | 9.6e-05 | 0.00807% | EFF Risk, CFO Other Risk
1162 | CADILLAC_RAR1090_EOL | 1.4361 | 0.021495 | 0.021495 | 3.8e-06 | 0.00807% | CFO Other Risk, EFF Risk
1163 | SAND CANYON_RAR0191_EOL | 0.74061 | 0.021464 | 0.021463 | 3.88e-06 | 0.00805% | CFO Other Risk, EFF Risk
1164 | HERZ_RAR0945_EOL | 1.5307 | 0.021425 | 0.021424 | 2.58e-05 | 0.00804% | EFF Risk, CFO Other Risk
1165 | HIGH SCHOOL_CB_RAR0043_RAR0042_ | 0.47119 | 0.021412 | 0.021411 | 8.72e-07 | 0.00803% | EFF Risk, CFO Other Risk
1166 | BROADCAST_PS0905_EOL | 2.6088 | 0.021395 | 0.021395 | 1.54e-07 | 0.00803% | CFO Other Risk, EFF Risk
1167 | DEVINE_RCS0169_EOL | 3.219 | 0.021392 | 0.021387 | 4.25e-05 | 0.00803% | EFF Risk, CFO Other Risk
1168 | BURGUNDY_RCS0007_EOL | 2.6034 | 0.021323 | 0.021319 | 1.59e-05 | 0.008% | EFF Risk, CFO Other Risk
1169 | AVANTI_RCS1365-2_PMH2034-4 | 2.1154 | 0.021273 | 0.021271 | 8.32e-05 | 0.00798% | EFF Risk, CFO Other Risk
1170 | BONNEVILLE_RAR9025_EOL | 6.543 | 0.02114 | 0.021139 | 8.18e-06 | 0.00793% | EFF Risk, CFO Other Risk
1171 | BELPAC_GS8076-5_RAR5512_PS6074_ | 3.315 | 0.021102 | 0.021085 | 0.00011503 | 0.00792% | EFF Risk, CFO Other Risk
1172 | GUITAR_RAR0386_RAR0041_RCS0387_ | 2.1017 | 0.021089 | 0.021089 | 2.9e-06 | 0.00791% | CFO Other Risk, EFF Risk
1173 | ANGELES_CB_RCS1947 | 4.2357 | 0.020913 | 0.02091 | 2e-05 | 0.00785% | EFF Risk, CFO Other Risk
1174 | SODA SPRINGS_RCS0541_RAR0480_RAR0879_ | 7.4152 | 0.020891 | 0.020888 | 4.56e-05 | 0.00784% | EFF Risk, CFO Other Risk
1175 | FELDSPAR_RCS1055_RCS0494 | 8.419 | 0.020874 | 0.020874 | 0.00012396 | 0.00783% | EFF Risk, CFO Other Risk
1176 | SUBIDA_CB_GS7155-4 | 0.74532 | 0.020829 | 0.020828 | 6.58e-06 | 0.00782% | EFF Risk, CFO Other Risk
1177 | VETERANS_PS6666_EOL | 0.46312 | 0.020753 | 0.020752 | 2.55e-06 | 0.00779% | EFF Risk, CFO Other Risk
1178 | DRISKILL_CB_RAR3883_GS0628-3_ | 1.1499 | 0.020689 | 0.020684 | 6.88e-06 | 0.00776% | EFF Risk, CFO Other Risk
1179 | BIDDER_PS7147_EOL | 2.0442 | 0.020679 | 0.020679 | 5.93e-07 | 0.00776% | EFF Risk, CFO Other Risk
1180 | RED BOX_RAR1484_EOL | 6.3356 | 0.020589 | 0.020589 | 1.15e-06 | 0.00773% | CFO Other Risk, EFF Risk
1181 | STATLER_RAR0346_PS0265 | 1.826 | 0.020586 | 0.020585 | 3.16e-05 | 0.00773% | EFF Risk, CFO VEG Risk
1182 | CONWAY_RAR0222_EOL | 10.9973 | 0.020552 | 0.020551 | 1.2e-06 | 0.00771% | EFF Risk, CFO Other Risk
1183 | SUCCESS_RAR0267_RAR3691 | 12.3698 | 0.020522 | 0.02052 | 6.21e-05 | 0.0077% | EFF Risk, CFO Other Risk
1184 | DALBA_RAR0016_EOL | 1.7684 | 0.020516 | 0.020515 | 3.65e-05 | 0.0077% | EFF Risk, CFO Other Risk
1185 | CARVER_RAR0452_EOL | 6.6481 | 0.020473 | 0.020473 | 4.11e-06 | 0.00768% | CFO Other Risk, EFF Risk
1186 | AGATE_RAR1275_EOL | 0.90414 | 0.020423 | 0.020422 | 1.07e-05 | 0.00766% | EFF Risk, CFO Other Risk
1187 | GREEN BEAR_RAR2118_EOL | 1.3115 | 0.020415 | 0.020414 | 1.95e-05 | 0.00766% | EFF Risk, CFO Other Risk
1188 | RICARDO_RSR0472_EOL | 0.55943 | 0.020399 | 0.020398 | 1.55e-05 | 0.00766% | EFF Risk, CFO Other Risk
1189 | THACHER_RAR0323_EOL | 2.0316 | 0.020378 | 0.020378 | 3.46e-06 | 0.00765% | EFF Risk, CFO Other Risk
1190 | AVENIDA_RAR0301_EOL | 2.3651 | 0.020335 | 0.020333 | 7.24e-05 | 0.00763% | EFF Risk, CFO Other Risk
1191 | GUITAR_RCS0387_RAR0402 | 4.2532 | 0.020226 | 0.020225 | 5.95e-06 | 0.00759% | CFO Other Risk, EFF Risk
1192 | DONNER_RCS2225_EOL | 0.362 | 0.02021 | 0.02021 | 3.82e-06 | 0.00758% | CFO Other Risk, EFF Risk
1193 | MORELLO_RAR0450_EOL | 3.6995 | 0.020208 | 0.020207 | 2.23e-06 | 0.00758% | EFF Risk, CFO Other Risk
1194 | CONEJO_CB_EOL | 1.4377 | 0.020198 | 0.020193 | 7.97e-05 | 0.00758% | EFF Risk, CFO Other Risk
1195 | PUFF_RCS7577_EOL | 2.4508 | 0.020198 | 0.020197 | 8.91e-07 | 0.00758% | EFF Risk, CFO Other Risk
1196 | PRONGHORN_RAR1263_RCS0028 | 3.9044 | 0.02013 | 0.020129 | 1.49e-05 | 0.00755% | CFO Other Risk, EFF Risk
1197 | HUGHES LAKE_CB_RAR1495_RAR0079_RAR0121 | 4.3618 | 0.020089 | 0.020084 | 8.44e-06 | 0.00754% | EFF Risk, CFO Other Risk
1198 | GLOBE MILLS_CB_GS1922-1 | 0.82353 | 0.020085 | 0.020084 | 2.7e-06 | 0.00754% | EFF Risk, CFO Other Risk
1199 | LANGER_CB_RCS0096 | 2.275 | 0.020055 | 0.020054 | 2.24e-05 | 0.00753% | EFF Risk, CFO Other Risk
1200 | GINGER_RCS0101_EOL | 4.9208 | 0.020054 | 0.020054 | 9.32e-06 | 0.00753% | CFO Other Risk, EFF Risk
1201 | DEALER_PS0044_EOL | 2.6898 | 0.02002 | 0.020019 | 1.27e-05 | 0.00751% | CFO Other Risk, EFF Risk
1202 | HACKLER_RSR9076_EOL | 2.5363 | 0.01998 | 0.019977 | 7.98e-05 | 0.0075% | EFF Risk, CFO Other Risk
1203 | TWIN LAKES_CB_RCS5233-2 | 1.9676 | 0.019902 | 0.019877 | 0.00012297 | 0.00747% | EFF Risk, CFO Other Risk
1204 | PINZON_RCS1049_EOL | 1.3913 | 0.019748 | 0.019747 | 2.67e-05 | 0.00741% | EFF Risk, CFO Other Risk
1205 | STEEL_RCS0218_EOL | 7.0949 | 0.019696 | 0.019696 | 3.47e-06 | 0.00739% | CFO Other Risk, EFF Risk
1206 | AMBERJACK_PME1315-2_EOL | 0.33968 | 0.019667 | 0.019667 | 2.77e-05 | 0.00738% | EFF Risk, CFO Other Risk
1207 | AMBRUS_RCS9673-1_EOL | 3.1821 | 0.019652 | 0.01965 | 0.00029713 | 0.00737% | EFF Risk, CFO Other Risk
1208 | TIMBER CANYON_PS1081_EOL | 4.1743 | 0.01959 | 0.01959 | 6.08e-06 | 0.00735% | EFF Risk, CFO Other Risk
1209 | LINNET_CB_RAR1694 | 2.6213 | 0.019588 | 0.019584 | 4.74e-05 | 0.00735% | EFF Risk, CFO Other Risk
1210 | SEABOARD_GS0573-3_EOL | 0.29552 | 0.019502 | 0.019502 | 2.12e-05 | 0.00732% | EFF Risk, CFO Other Risk
1211 | SOCRATES_RAR0792_EOL | 2.7583 | 0.019475 | 0.019474 | 2.21e-05 | 0.00731% | CFO Other Risk, EFF Risk
1212 | JARVIS_RAR0992_EOL | 17.6489 | 0.019465 | 0.019461 | 4.36e-05 | 0.0073% | CFO Other Risk, EFF Risk
1213 | RED MOUNTAIN_CB_PS0094 | 2.3739 | 0.019391 | 0.01939 | 2.74e-06 | 0.00728% | EFF Risk, CFO Other Risk
1214 | CALSPAR_PS0161_EOL | 0.29921 | 0.01935 | 0.019349 | 5.43e-06 | 0.00726% | EFF Risk, CFO Other Risk
1215 | CEYLON_GS3087-2_EOL | 1.3359 | 0.019347 | 0.019346 | 1.45e-05 | 0.00726% | EFF Risk, CFO Other Risk
1216 | SEXTON_PS0020_EOL | 0.66112 | 0.019308 | 0.019307 | 1.86e-05 | 0.00725% | EFF Risk, CFO Other Risk
1217 | CRESTLINE_PS0711_EOL | 1.273 | 0.019292 | 0.01929 | 1.44e-05 | 0.00724% | EFF Risk, CFO Other Risk
1218 | ANACONDA_CB_RCS0119 | 1.1642 | 0.019209 | 0.019203 | 6.01e-05 | 0.00721% | CFO Other Risk, EFF Risk
1219 | HONEYCRISP_GS1423-2_PS2948 | 0.97403 | 0.019136 | 0.019129 | 6.05e-05 | 0.00718% | EFF Risk, CFO Other Risk
1220 | CACHUMA_RAR0563_EOL | 6.0663 | 0.019069 | 0.019064 | 5.09e-05 | 0.00716% | CFO Other Risk, EFF Risk
1221 | MORITZ_RAR1051_EOL | 0.99269 | 0.018983 | 0.018981 | 1.45e-05 | 0.00712% | EFF Risk, CFO Other Risk
1222 | PAWLEY_RAR0451_EOL | 15.217 | 0.018972 | 0.018968 | 5.99e-05 | 0.00712% | CFO Other Risk, EFF Risk
1223 | SECO_CB_PS0529 [2] | 0.74997 | 0.018958 | 0.018954 | 6.75e-06 | 0.00711% | EFF Risk, CFO Other Risk
1224 | WELCH_PS3244_EOL | 4.6192 | 0.018907 | 0.018907 | 3.89e-06 | 0.0071% | EFF Risk, CFO Other Risk
1225 | COLLINS_CB_EOL | 0.79339 | 0.01887 | 0.018861 | 0.00014479 | 0.00708% | EFF Risk, CFO Other Risk
1226 | ACOSTA_RCS0879-1_GS5494-1_PME4585-2_ | 1.9513 | 0.018819 | 0.018801 | 6.21e-05 | 0.00706% | EFF Risk, CFO Other Risk
1227 | ROCKRIDGE_GS5448-1_PS1414 | 1.8443 | 0.018755 | 0.018753 | 3.85e-05 | 0.00704% | EFF Risk, CFO Other Risk
1228 | LA MANCHA_CB_RAR0208_RAR0781_ | 0.67112 | 0.018732 | 0.018732 | 8.91e-06 | 0.00703% | EFF Risk, CFO Other Risk
1229 | PINE COVE_RCS8993_EOL | 3.265 | 0.018653 | 0.018652 | 2.07e-05 | 0.007% | EFF Risk, CFO Other Risk
1230 | ROSA_RCS3452-2_EOL | 3.6871 | 0.018568 | 0.018568 | 9.09e-05 | 0.00697% | EFF Risk, CFO Other Risk
1231 | SHERBOURNE_CB_PS0007 | 4.411 | 0.018522 | 0.018522 | 2.26e-05 | 0.00695% | EFF Risk, CFO Other Risk
1232 | THACHER_RSR0053_RAR0323_RAR0096_ | 4.5498 | 0.018512 | 0.018511 | 7.75e-06 | 0.00695% | EFF Risk, CFO Other Risk
1233 | SNOW VALLEY_RAR1987_EOL | 1.6074 | 0.018482 | 0.01848 | 3.03e-05 | 0.00694% | EFF Risk, CFO Other Risk
1234 | SKINNER_PS1343_EOL | 2.2888 | 0.018339 | 0.018339 | 2.4e-10 | 0.00688% | EFF Risk, CFO Other Risk
1235 | UNDERWOOD_RAR0009_RCS0363 | 3.7479 | 0.018328 | 0.018326 | 3.99e-06 | 0.00688% | EFF Risk, CFO Other Risk
1236 | AVENGER_RCS2240_RAR2242_RAR2241_ | 5.7439 | 0.018313 | 0.018312 | 5.12e-05 | 0.00687% | EFF Risk, CFO Other Risk
1237 | DUKE_CB_RCS0968_RAR0534_ | 0.58816 | 0.018304 | 0.018301 | 7.59e-06 | 0.00687% | EFF Risk, CFO Other Risk
1238 | SQUINT_CB_RAR0765 | 5.316 | 0.018271 | 0.018264 | 1.74e-05 | 0.00686% | EFF Risk, CFO Other Risk
1239 | MIST_RAR0306_RAR0392_RAR9675_ | 7.6918 | 0.01823 | 0.018228 | 5.07e-06 | 0.00684% | EFF Risk, CFO Other Risk
1240 | PINTO_RCS0309_RAR0341 | 0.38752 | 0.018186 | 0.018186 | 1.45e-08 | 0.00682% | CFO Other Risk, EFF Risk
1241 | COPPERHEAD_CB_EOL | 0.79367 | 0.018109 | 0.018107 | 0.00012588 | 0.0068% | EFF Risk, CFO Other Risk
1242 | INTAKE_RAR0785_EOL | 9.4457 | 0.018035 | 0.018035 | 5.27e-06 | 0.00677% | EFF Risk, CFO Other Risk
1243 | NORTHPARK_RCS2113_RCS1998-1_RAR0824_ | 2.3434 | 0.017958 | 0.017951 | 4.01e-05 | 0.00674% | EFF Risk, CFO Other Risk
1244 | CARMELITA_RCS2012_BF00112 | 3.4894 | 0.017822 | 0.017813 | 5.89e-05 | 0.00669% | EFF Risk, CFO Other Risk
1245 | CUTHBERT_BF05638_EOL | 0.45238 | 0.017777 | 0.017776 | 6.66e-06 | 0.00667% | EFF Risk, CFO Other Risk
1246 | REED_RAR1165_EOL | 1.1916 | 0.017711 | 0.01771 | 2.5e-05 | 0.00665% | CFO Other Risk, EFF Risk
1247 | SHORELINE_CB_EOL | 1.3537 | 0.01768 | 0.01768 | 2.11e-06 | 0.00663% | EFF Risk, CFO Other Risk
1248 | ESTABAN_RAR9580_EOL | 4.3701 | 0.017666 | 0.017662 | 4.04e-05 | 0.00663% | EFF Risk, CFO Other Risk
1249 | TATANKA_RAR0531_EOL | 0.72697 | 0.017649 | 0.017649 | 4.36e-07 | 0.00662% | EFF Risk, CFO Other Risk
1250 | HUGHES LAKE_RAR0079_EOL | 5.6898 | 0.017558 | 0.017556 | 6.83e-06 | 0.00659% | EFF Risk, CFO Other Risk
1251 | KUFFEL_RAR0020_EOL | 3.7337 | 0.01754 | 0.017534 | 3.72e-05 | 0.00658% | EFF Risk, CFO Other Risk
1252 | QUICKSILVER_RSR0177_EOL | 5.7821 | 0.017516 | 0.017513 | 5.45e-05 | 0.00657% | EFF Risk, CFO Other Risk
1253 | RAVINE_CB_EOL | 12.0061 | 0.017492 | 0.017477 | 2.94e-05 | 0.00656% | EFF Risk, CFO Other Risk
1254 | JORDAN_RAR0841_PS0839 | 9.2621 | 0.017453 | 0.017453 | 4.85e-06 | 0.00655% | EFF Risk, CFO Other Risk
1255 | HUGO_CB_EOL | 0.83746 | 0.017292 | 0.017292 | 1.08e-06 | 0.00649% | EFF Risk, CFO Other Risk
1256 | LANE_CB_RAR0919 | 0.6349 | 0.017239 | 0.017239 | 2.16e-06 | 0.00647% | EFF Risk, CFO Other Risk
1257 | ROBINSON CREEK_CB_RAR0154 | 5.8887 | 0.017232 | 0.017229 | 1.24e-05 | 0.00647% | EFF Risk, CFO Other Risk
1258 | APPLETON_CB_PS0059 | 2.4588 | 0.01719 | 0.017186 | 1.63e-05 | 0.00645% | EFF Risk, CFO Other Risk
1259 | DEVILS GATE_CB_PS0552 | 3.4182 | 0.017159 | 0.017157 | 1.24e-05 | 0.00644% | EFF Risk, CFO Other Risk
1260 | SALT CREEK_RAR0671_EOL | 5.7941 | 0.017157 | 0.017156 | 1.4e-05 | 0.00644% | EFF Risk, CFO Other Risk
1261 | CARLET_RAR0623_EOL | 2.7188 | 0.017153 | 0.017152 | 2.57e-05 | 0.00644% | EFF Risk, CFO Other Risk
1262 | LAUDA_RAR9037_EOL | 1.1602 | 0.017124 | 0.017124 | 4.76e-08 | 0.00643% | CFO Other Risk, EFF Risk
1263 | NERO_CB_PS0401 | 0.58542 | 0.017123 | 0.017122 | 6.22e-06 | 0.00643% | EFF Risk, CFO Other Risk
1264 | GUARD_CB_PME1726-2 | 1.4812 | 0.017049 | 0.017049 | 1.9e-05 | 0.0064% | EFF Risk, CFO Other Risk
1265 | TORONTO_RAR0872_EOL | 3.7374 | 0.017039 | 0.017035 | 3.52e-05 | 0.00639% | EFF Risk, CFO Other Risk
1266 | RANKIN_RAR0722_EOL | 3.133 | 0.01703 | 0.01703 | 1.37e-06 | 0.00639% | EFF Risk, CFO Other Risk
1267 | MALAGA COVE_CB_EOL | 1.0869 | 0.016941 | 0.01694 | 1.58e-05 | 0.00636% | EFF Risk, CFO Other Risk
1268 | ACRES_RCS0530_EOL | 2.7277 | 0.01694 | 0.016938 | 9.08e-05 | 0.00636% | EFF Risk, CFO Other Risk
1269 | BORCHARD_CB_RAR0115_GS0863-3_ | 1.7934 | 0.016908 | 0.016906 | 1.32e-05 | 0.00634% | EFF Risk, CFO Other Risk
1270 | SNOW VALLEY_RAR0605_RCS0568_RAR0025_ | 1.694 | 0.016893 | 0.016889 | 3.41e-05 | 0.00634% | EFF Risk, CFO Other Risk
1271 | CELLO_PS4253_EOL | 1.2909 | 0.016847 | 0.016842 | 3.04e-05 | 0.00632% | EFF Risk, CFO Other Risk
1272 | TWIN PEAKS_RAR1053_EOL | 0.47082 | 0.016838 | 0.016838 | 0 | 0.00632% | EFF Risk, CFO Other Risk
1273 | ARCTURUS_CB_EOL | 2.8277 | 0.016798 | 0.016796 | 5.46e-05 | 0.0063% | EFF Risk, CFO Other Risk
1274 | SKY HI_RAR1322_EOL | 2.9636 | 0.016585 | 0.016584 | 2.65e-05 | 0.00622% | CFO Other Risk, EFF Risk
1275 | CANET_RCS4272-4_EOL | 3.7449 | 0.016503 | 0.016497 | 1.93e-05 | 0.00619% | EFF Risk, CFO Other Risk
1276 | O'TOOLE_CB_EOL | 4.674 | 0.016384 | 0.016381 | 9.13e-05 | 0.00615% | EFF Risk, CFO Other Risk
1277 | PENSTOCK_RCS0596_EOL | 1.7564 | 0.01637 | 0.016369 | 4.32e-06 | 0.00614% | CFO Other Risk, EFF Risk
1278 | MORITZ_CB_RAR1051_RAR0338_RAR0364 | 1.5195 | 0.016328 | 0.016325 | 2.26e-05 | 0.00613% | EFF Risk, CFO Other Risk
1279 | SNOW VALLEY_RCS0560_RAR1987 | 1.2313 | 0.016259 | 0.016256 | 2.49e-05 | 0.0061% | EFF Risk, CFO Other Risk
1280 | SERRA_PS0243_RCS0151 | 1.0948 | 0.016199 | 0.016199 | 5.21e-07 | 0.00608% | CFO Other Risk, EFF Risk
1281 | KINSEY_PS0719_EOL | 7.7791 | 0.01612 | 0.01612 | 2.25e-06 | 0.00605% | EFF Risk, CFO Other Risk
1282 | HAMMERHEAD_CB_RCS1875 | 0.52091 | 0.016054 | 0.016053 | 2.16e-05 | 0.00602% | EFF Risk, CFO Other Risk
1283 | KINSEY_RAR1468_RAR0452_RAR0302_ | 8.5162 | 0.016039 | 0.016038 | 2.46e-06 | 0.00602% | EFF Risk, CFO Other Risk
1284 | SCIURBA_RCS1122_EOL | 7.5248 | 0.016004 | 0.016001 | 0.0002045 | 0.00601% | EFF Risk, CFO VEG Risk
1285 | FIREBIRD_CB_BF31047_RSR0552_ | 0.63271 | 0.016002 | 0.016002 | 4.78e-06 | 0.006% | EFF Risk, CFO Other Risk
1286 | SODA SPRINGS_RCS0505_EOL | 6.475 | 0.015971 | 0.015968 | 3.95e-05 | 0.00599% | EFF Risk, CFO Other Risk
1287 | BIDDER_RCS5163_PS7147 | 7.429 | 0.015897 | 0.015896 | 2.1e-06 | 0.00597% | EFF Risk, CFO Other Risk
1288 | DOBLE_CB_RCS0342 | 9.9765 | 0.015854 | 0.015853 | 6.75e-07 | 0.00595% | EFF Risk, CFO Other Risk
1289 | HILLFIELD_RCS3816_EOL | 4.9827 | 0.015848 | 0.015843 | 8.21e-05 | 0.00595% | EFF Risk, CFO Other Risk
1290 | FLYING D_RAR0610_RAR0663_RCS0708_ | 2.6203 | 0.015824 | 0.015824 | 2.35e-06 | 0.00594% | EFF Risk, CFO Other Risk
1291 | SHOPPER_RCS4321_EOL | 2.1282 | 0.015785 | 0.015784 | 1.07e-05 | 0.00592% | CFO Other Risk, EFF Risk
1292 | DICE_RCS0390_EOL | 3.2001 | 0.015766 | 0.015766 | 4.2e-08 | 0.00592% | EFF Risk, CFO Other Risk
1293 | TWIN PEAKS_RCS0435_RAR1053 | 1.4423 | 0.015652 | 0.015652 | 0 | 0.00587% | EFF Risk, CFO Other Risk
1294 | VIAVERDE_PS0180_EOL | 1.5944 | 0.015616 | 0.015615 | 1.78e-05 | 0.00586% | EFF Risk, CFO Other Risk
1295 | HI LINE_RAR0059_RCS0035 | 7.0634 | 0.015588 | 0.015588 | 3.6e-06 | 0.00585% | EFF Risk, CFO Other Risk
1296 | COOLER_RCS4314-4_EOL | 0.64014 | 0.015576 | 0.015576 | 5.46e-05 | 0.00585% | EFF Risk, CFO Other Risk
1297 | CUTHBERT_RCS1692-1_EOL | 0.36196 | 0.01557 | 0.015569 | 5.46e-06 | 0.00584% | CFO Other Risk, EFF Risk
1298 | SUCCESS_RAR0491_RAR0267 | 5.0749 | 0.015517 | 0.015516 | 3.47e-05 | 0.00582% | EFF Risk, CFO Other Risk
1299 | PETIT_RAR9591_EOL | 0.538 | 0.015497 | 0.015497 | 5.75e-07 | 0.00582% | EFF Risk, CFO Other Risk
1300 | VIDEO_CB_RAR0927_RAR1716_ [2] | 0.8983 | 0.015495 | 0.015495 | 4.07e-06 | 0.00581% | EFF Risk, CFO Other Risk
1301 | YUCATAN_CB_PS0991 | 0.95749 | 0.01543 | 0.015429 | 1.58e-05 | 0.00579% | EFF Risk, CFO Other Risk
1302 | RESORT_RAR1012_RCS8919 | 4.2449 | 0.015385 | 0.015385 | 1.34e-07 | 0.00577% | CFO Other Risk, EFF Risk
1303 | CAREY_RAR1168_EOL | 1.0198 | 0.015368 | 0.015368 | 3.74e-05 | 0.00577% | EFF Risk, CFO Other Risk
1304 | NASHVILLE_RCS1160-1_EOL | 3.2448 | 0.015361 | 0.015357 | 3.53e-05 | 0.00576% | EFF Risk, CFO Other Risk
1305 | WINNEBAGO_RSR5499_GS6639-3 | 2.0927 | 0.015338 | 0.015335 | 4.64e-05 | 0.00576% | EFF Risk, CFO Other Risk
1306 | INTERIOR_RCS0032_EOL | 3.5343 | 0.015317 | 0.015316 | 3.27e-05 | 0.00575% | EFF Risk, CFO Other Risk
1307 | NIGHTHAWK_CB_EOL | 3.0308 | 0.015107 | 0.015106 | 1.19e-05 | 0.00567% | CFO Other Risk, EFF Risk
1308 | INTERIOR_RAR0043_RCS0032_RAR0005_ | 14.0331 | 0.0151 | 0.015096 | 0.00013046 | 0.00567% | CFO Other Risk, EFF Risk
1309 | INTREPID_CB_RCS8119-1 | 6.1973 | 0.015083 | 0.015071 | 0.00061515 | 0.00566% | EFF Risk, CFO Other Risk
1310 | CROWLEY_RCS0257_EOL | 5.2423 | 0.015053 | 0.015051 | 4.49e-06 | 0.00565% | EFF Risk, CFO Other Risk
1311 | MIRAMAR_CB_EOL | 1.9788 | 0.014989 | 0.014988 | 1.36e-05 | 0.00562% | EFF Risk, CFO Other Risk
1312 | VERDEMONT_RCS0833_EOL | 1.6478 | 0.014984 | 0.014984 | 8.69e-08 | 0.00562% | EFF Risk, CFO Other Risk
1313 | CALGROVE_RCS3916_PS2004 | 1.7132 | 0.014901 | 0.014899 | 7.13e-06 | 0.00559% | CFO Other Risk, EFF Risk
1314 | SITZMARK_RCS0300_EOL | 1.8911 | 0.014763 | 0.014747 | 4.31e-05 | 0.00554% | EFF Risk, CFO Other Risk
1315 | CHARLTON_RAR1616_EOL | 1.7753 | 0.014728 | 0.014727 | 1.95e-05 | 0.00553% | EFF Risk, CFO Other Risk
1316 | DALBA_RAR0032_EOL | 1.8734 | 0.014707 | 0.014704 | 4.01e-05 | 0.00552% | EFF Risk, CFO Other Risk
1317 | POTATO_RAR0889_EOL | 2.0408 | 0.014698 | 0.014697 | 0.0001405 | 0.00552% | EFF Risk, CFO Other Risk
1318 | BOMBAY_RCS5543-1_GS5532-3 | 2.7114 | 0.014687 | 0.014687 | 5.8e-06 | 0.00551% | EFF Risk, CFO Other Risk
1319 | COBRA_RCS4245-3_RCS1448-2 | 0.38434 | 0.014664 | 0.014663 | 1.65e-05 | 0.0055% | CFO Other Risk, EFF Risk
1320 | SHAKE_CB_PS0419 | 2.6614 | 0.014659 | 0.014659 | 0 | 0.0055% | EFF Risk, CFO Other Risk
1321 | BIRCHIM_RAR0207_EOL | 4.1406 | 0.0146 | 0.014598 | 5.84e-06 | 0.00548% | EFF Risk, CFO Other Risk
1322 | LARCH_RCS0862_RCS0849 | 2.1419 | 0.014504 | 0.014504 | 5.07e-07 | 0.00544% | EFF Risk, CFO Other Risk
1323 | POLYMER_CB_EOL | 1.0099 | 0.014462 | 0.014462 | 1.46e-06 | 0.00543% | CFO Other Risk, EFF Risk
1324 | HOVATTER_CB_RCS0799 | 3.2192 | 0.014322 | 0.01432 | 1.68e-05 | 0.00537% | EFF Risk, CFO Other Risk
1325 | SLOPE_CB_EOL | 1.8633 | 0.014251 | 0.014211 | 7.33e-05 | 0.00535% | EFF Risk, CFO Other Risk
1326 | STEARNS_CB_RCS9871 | 3.0084 | 0.014214 | 0.014203 | 4.99e-05 | 0.00533% | EFF Risk, CFO Other Risk
1327 | CASTRO_RAR1101_EOL | 3.8486 | 0.014198 | 0.014196 | 3.46e-05 | 0.00533% | EFF Risk, CFO Other Risk
1328 | QUICKSILVER_RAR0324_EOL | 0.66263 | 0.014121 | 0.014121 | 6.09e-06 | 0.0053% | CFO Other Risk, EFF Risk
1329 | MORITZ_RAR0338_RCS0375_RCS0590_ | 2.0802 | 0.014077 | 0.014073 | 3.03e-05 | 0.00528% | EFF Risk, CFO Other Risk
1330 | HORIZON_CB_RAR5174_RAR3846_ | 3.3443 | 0.014071 | 0.014071 | 2.79e-05 | 0.00528% | EFF Risk, CFO Other Risk
1331 | BEAR VALLEY_RAR0519_EOL | 3.6504 | 0.014065 | 0.014065 | 7.14e-07 | 0.00528% | EFF Risk, CFO Other Risk
1332 | WHITECLIFF_RCS5902_EOL | 3.0809 | 0.014063 | 0.014052 | 5.2e-05 | 0.00528% | EFF Risk, CFO Other Risk
1333 | RAINBOW_BF39986_EOL | 0.76163 | 0.014033 | 0.014033 | 8.84e-07 | 0.00527% | EFF Risk, CFO Other Risk
1334 | AGATE_RCS0791_RCS0263_RAR1275_ | 1.8468 | 0.014021 | 0.014018 | 2.36e-05 | 0.00526% | CFO Other Risk, EFF Risk
1335 | TANDEM_PS0121_EOL | 1.6362 | 0.014008 | 0.014008 | 1.3e-05 | 0.00526% | EFF Risk, CFO Other Risk
1336 | MEBANE_CB_EOL | 4.6228 | 0.013984 | 0.013984 | 1.84e-06 | 0.00525% | EFF Risk, CFO Other Risk
1337 | TEE VEE_CB_EOL | 4.7793 | 0.013959 | 0.013959 | 3.49e-07 | 0.00524% | EFF Risk, CFO Other Risk
1338 | SKYBORNE_RAR0804_EOL | 3.2863 | 0.013902 | 0.013901 | 1.55e-05 | 0.00522% | EFF Risk, CFO Other Risk
1339 | SAVORY_RAR7187_RAR1058 | 2.0917 | 0.013895 | 0.013895 | 7.87e-07 | 0.00521% | EFF Risk, CFO Other Risk
1340 | NORTH BAY_RAR0013_EOL | 2.5715 | 0.013894 | 0.013892 | 2.33e-05 | 0.00521% | EFF Risk, CFO Other Risk
1341 | CROWLEY_RCS0285_RCS0257 | 4.1674 | 0.013824 | 0.013822 | 3.51e-06 | 0.00519% | EFF Risk, CFO Other Risk
1342 | HOT SPRINGS_PS0525_RCS1908-2 | 3.7014 | 0.013783 | 0.013767 | 7.91e-05 | 0.00517% | EFF Risk, CFO Other Risk
1343 | CALGROVE_RCS0072_RCS6552-3 | 2.3781 | 0.013746 | 0.013744 | 8.87e-06 | 0.00516% | CFO Other Risk, EFF Risk
1344 | TECOLOTE_RCS0046_EOL | 1.1773 | 0.013688 | 0.013671 | 3.3e-05 | 0.00514% | EFF Risk, CFO Other Risk
1345 | JENKS LAKE_RAR0541_RCS0504 | 3.7732 | 0.013652 | 0.013652 | 5.84e-06 | 0.00512% | EFF Risk, CFO Other Risk
1346 | MAMBA_CB_RCS3596-2 | 0.62572 | 0.01361 | 0.013609 | 4.69e-06 | 0.00511% | CFO Other Risk, EFF Risk
1347 | VERDEMONT_CB_RCS0823 | 1.8402 | 0.013542 | 0.013542 | 1.43e-07 | 0.00508% | EFF Risk, CFO Other Risk
1348 | THACHER_RSR9630_RAR0174 | 1.4115 | 0.013517 | 0.013517 | 2.41e-06 | 0.00507% | EFF Risk, CFO Other Risk
1349 | CUYAMA_RAR0757_RAR0770 | 13.6922 | 0.013466 | 0.013465 | 2.79e-06 | 0.00505% | EFF Risk, CFO Other Risk
1350 | KINGSFORD_RCS0277_EOL | 1.0143 | 0.013457 | 0.013456 | 1.79e-05 | 0.00505% | EFF Risk, CFO Other Risk
1351 | PARSONS_GS6396-3_EOL | 0.29425 | 0.013429 | 0.013429 | 6.04e-06 | 0.00504% | CFO Other Risk, EFF Risk
1352 | BUCKHORN_RAR0404_EOL | 1.3343 | 0.013406 | 0.013405 | 4.06e-06 | 0.00503% | EFF Risk, CFO Other Risk
1353 | JENKS LAKE_PS0502_RAR0541 | 3.4793 | 0.013349 | 0.013349 | 5.38e-06 | 0.00501% | EFF Risk, CFO Other Risk
1354 | MALOY_CB_RCS0244 | 1.7995 | 0.013341 | 0.01334 | 3.4e-06 | 0.00501% | EFF Risk, CFO Other Risk
1355 | BUFFER_RAR0330_EOL | 1.3805 | 0.013215 | 0.013213 | 2.46e-05 | 0.00496% | CFO Other Risk, EFF Risk
1356 | ARLINGTON_CB_PS3133 | 1.2697 | 0.013197 | 0.013197 | 1.4e-05 | 0.00495% | CFO Other Risk, EFF Risk
1357 | CHATEAU_CB_EOL | 0.83767 | 0.013194 | 0.013194 | 0 | 0.00495% | EFF Risk, CFO Other Risk
1358 | GRANDAD_CB_RAR0051 | 5.7714 | 0.013144 | 0.013144 | 8.23e-07 | 0.00493% | EFF Risk, CFO Other Risk
1359 | HURLEY_RCS0123_EOL | 2.9254 | 0.013104 | 0.013092 | 2.41e-05 | 0.00492% | EFF Risk, CFO Other Risk
1360 | APPLETON_PS0059_EOL | 6.4852 | 0.013096 | 0.013087 | 4.24e-05 | 0.00491% | EFF Risk, CFO Other Risk
1361 | CRAB_RCS0428_EOL | 0.40169 | 0.013084 | 0.013084 | 1.76e-08 | 0.00491% | EFF Risk, CFO Other Risk
1362 | LA MANCHA_RAR0208_EOL | 0.85552 | 0.01305 | 0.01305 | 1.13e-05 | 0.0049% | EFF Risk, CFO Other Risk
1363 | CRAWFORD_CB_EOL | 0.60932 | 0.013043 | 0.01304 | 3.87e-06 | 0.00489% | EFF Risk, CFO VEG Risk
1364 | CASTRO_CB_RCS1417 | 0.42196 | 0.013037 | 0.013033 | 7.47e-06 | 0.00489% | EFF Risk, CFO Other Risk
1365 | PRONGHORN_RAR1079_EOL | 1.1343 | 0.012968 | 0.012967 | 4.48e-06 | 0.00487% | EFF Risk, CFO Other Risk
1366 | WEESHA_CB_PS0244_PD0219_ | 0.63143 | 0.012959 | 0.012958 | 1.18e-06 | 0.00486% | EFF Risk, CFO Other Risk
1367 | TULLY_RCS1000_EOL | 2.0632 | 0.012902 | 0.012899 | 2.78e-05 | 0.00484% | EFF Risk, CFO Other Risk
1368 | BOBBY_PS0835_EOL | 2.2924 | 0.012901 | 0.0129 | 2.35e-05 | 0.00484% | CFO Other Risk, EFF Risk
1369 | TIN MINE_RAR7265_EOL | 2.0959 | 0.012894 | 0.012894 | 2.24e-05 | 0.00484% | EFF Risk, CFO Other Risk
1370 | BLACKBIRD_GS7865-3_EOL | 0.99901 | 0.012867 | 0.012867 | 2.69e-05 | 0.00483% | CFO Other Risk, EFF Risk
1371 | PINWHEEL_CB_EOL | 2.5127 | 0.012844 | 0.012844 | 5.4e-07 | 0.00482% | EFF Risk, CFO Other Risk
1372 | KINSEY_CB_RAR1468_RCS0708_ | 2.2979 | 0.012831 | 0.012831 | 6.65e-07 | 0.00482% | EFF Risk, CFO Other Risk
1373 | SUSAN_RAR2566_EOL | 1.0933 | 0.012829 | 0.012827 | 1.36e-05 | 0.00481% | EFF Risk, CFO Other Risk
1374 | CONCEPCION_RAR0612_RAR2129 | 4.9845 | 0.012779 | 0.012778 | 6.67e-06 | 0.0048% | EFF Risk, CFO Other Risk
1375 | HENDERSON_RCS1692_EOL | 4.6529 | 0.012696 | 0.012695 | 7.38e-06 | 0.00476% | EFF Risk, CFO Other Risk
1376 | GUTIERREZ_CB_EOL | 3.9453 | 0.012669 | 0.012663 | 2.21e-05 | 0.00475% | EFF Risk, CFO Other Risk
1377 | MUSTANG_CB_PS0614 | 1.3798 | 0.012625 | 0.012624 | 1.53e-06 | 0.00474% | EFF Risk, CFO Other Risk
1378 | TENNECO_RAR0765_EOL | 5.6119 | 0.012591 | 0.012587 | 4.35e-05 | 0.00472% | EFF Risk, CFO Other Risk
1379 | BUCKHORN_RCS1501_RSR3065 | 1.6775 | 0.012571 | 0.01257 | 5.13e-06 | 0.00472% | EFF Risk, CFO Other Risk
1380 | YUCATAN_PS0991_EOL | 0.92009 | 0.012569 | 0.012568 | 1.49e-05 | 0.00472% | CFO Other Risk, EFF Risk
1381 | HIGHBALL_PS6699_EOL | 1.7881 | 0.012555 | 0.012553 | 8.22e-06 | 0.00471% | EFF Risk, CFO Other Risk
1382 | VENUS_CB_EOL | 8.1053 | 0.012484 | 0.012482 | 0.00013892 | 0.00468% | EFF Risk, CFO Other Risk
1383 | CRUMP_RCS0638_EOL | 1.1963 | 0.012351 | 0.01235 | 1.65e-05 | 0.00464% | EFF Risk, CFO Other Risk
1384 | RACER_BF59097_EOL | 0.91114 | 0.012313 | 0.012313 | 1.59e-05 | 0.00462% | CFO Other Risk, EFF Risk
1385 | TIPS_RCS7865-2_EOL | 0.35973 | 0.012304 | 0.012302 | 2.2e-05 | 0.00462% | EFF Risk, CFO Other Risk
1386 | CANTINA_CB_RCS4443-2_RCS4443-1_ | 1.49 | 0.012297 | 0.012293 | 9.6e-05 | 0.00461% | EFF Risk, CFO Other Risk
1387 | POWER_CB_EOL | 0.86466 | 0.01229 | 0.01229 | 3.69e-06 | 0.00461% | EFF Risk, CFO Other Risk
1388 | JUBILEE_CB_PS0315 | 0.54532 | 0.012286 | 0.012285 | 3.46e-06 | 0.00461% | EFF Risk, CFO Other Risk
1389 | CUERVO_RCS7020-3_EOL | 0.34393 | 0.012246 | 0.012246 | 9.07e-06 | 0.0046% | EFF Risk, CFO Other Risk
1390 | TENNECO_RAR0764_EOL | 4.6043 | 0.012231 | 0.012228 | 3.57e-05 | 0.00459% | EFF Risk, CFO Other Risk
1391 | SODA SPRINGS_CB_RAR0873_RAR0538_RAR0532 | 4.1143 | 0.012216 | 0.012214 | 3.16e-05 | 0.00458% | EFF Risk, CFO Other Risk
1392 | INDEPENDENCE_CB_RCS1355 | 0.78528 | 0.012197 | 0.012189 | 0.00020683 | 0.00458% | EFF Risk, CFO Other Risk
1393 | TROUT_RCS0369-1_EOL | 1.5507 | 0.012148 | 0.012148 | 2.27e-08 | 0.00456% | EFF Risk, CFO Other Risk
1394 | STROH_CB_EOL | 0.73814 | 0.012122 | 0.012122 | 5.63e-06 | 0.00455% | EFF Risk, CFO Other Risk
1395 | ROSEBUD_RAR0279_EOL | 7.9172 | 0.01212 | 0.012118 | 7.3e-06 | 0.00455% | EFF Risk, CFO Other Risk
1396 | LEVECHE_PS0864_RSR0479 | 1.5692 | 0.012111 | 0.012105 | 1.47e-05 | 0.00454% | CFO Other Risk, EFF Risk
1397 | TEJON_PS0528_PS0529_PS0887_ | 2.6868 | 0.012086 | 0.012085 | 3.92e-06 | 0.00454% | CFO Other Risk, EFF Risk
1398 | CONINE_CB_RSR1128 | 0.41867 | 0.012012 | 0.01201 | 7.28e-06 | 0.00451% | EFF Risk, CFO Other Risk
1399 | HOSPITAL_RCS3031_EOL | 2.5663 | 0.011975 | 0.011973 | 1.41e-05 | 0.00449% | EFF Risk, CFO Other Risk
1400 | DOBLE_RCS0342_EOL | 4.8256 | 0.011974 | 0.011974 | 2.22e-07 | 0.00449% | EFF Risk, CFO Other Risk
1401 | TAGGERT_RAR0623_EOL | 1.9135 | 0.011937 | 0.011936 | 2.39e-05 | 0.00448% | CFO Other Risk, EFF Risk
1402 | CANAL_RAR1025_RCS1709 | 4.3048 | 0.011924 | 0.011924 | 3.06e-08 | 0.00447% | EFF Risk, CFO Other Risk
1403 | CIRCLE_CB_RCS1133_RAR1069_ | 0.776 | 0.011913 | 0.011913 | 9.2e-07 | 0.00447% | CFO Other Risk, EFF Risk
1404 | ENCANTO_RCS0375_PS0147 | 2.053 | 0.011848 | 0.011837 | 3.3e-05 | 0.00445% | EFF Risk, CFO Other Risk
1405 | BOULDER_CB_RCS1090-1_RAR0240_PS0241 | 0.89901 | 0.011841 | 0.01184 | 1.05e-05 | 0.00444% | EFF Risk, CFO Other Risk
1406 | BIANCO_PS8707_EOL | 0.80209 | 0.011789 | 0.011788 | 9.42e-06 | 0.00442% | EFF Risk, CFO Other Risk
1407 | HELENA_PS6004_EOL | 2.8364 | 0.011752 | 0.011748 | 6.47e-05 | 0.00441% | EFF Risk, CFO Other Risk
1408 | CASCADA_CB_EOL | 1.7456 | 0.011737 | 0.011736 | 4.32e-06 | 0.0044% | CFO Other Risk, EFF Risk
1409 | CASSIDY_CB_RCS1246-2 | 2.4082 | 0.011733 | 0.011726 | 6.1e-05 | 0.0044% | EFF Risk, CFO Other Risk
1410 | SWIFT_CB_RCS0462 | 1.2297 | 0.011725 | 0.011724 | 3.19e-06 | 0.0044% | EFF Risk, CFO Other Risk
1411 | DEALER_PS1003_EOL | 2.6444 | 0.011706 | 0.011705 | 1.74e-05 | 0.00439% | EFF Risk, CFO Other Risk
1412 | MONTGOMERY_CB_EOL | 6.4773 | 0.011697 | 0.011682 | 0.00010895 | 0.00439% | EFF Risk, CFO Other Risk
1413 | CONFERENCE_CB_EOL | 0.80009 | 0.011645 | 0.011645 | 1.34e-07 | 0.00437% | EFF Risk, CFO Other Risk
1414 | JORDAN_RAR0844_EOL | 4.2275 | 0.011594 | 0.011594 | 2.2e-06 | 0.00435% | EFF Risk, CFO Other Risk
1415 | CHINA PEAK_RAR0934_EOL | 4.4437 | 0.01156 | 0.01156 | 6.45e-06 | 0.00434% | EFF Risk, CFO Other Risk
1416 | HELENKA_CB_RAR1232 | 0.43358 | 0.011533 | 0.011533 | 1.5e-06 | 0.00433% | CFO Other Risk, EFF Risk
1417 | SKINKLE_RCS0244_EOL | 7.5812 | 0.011392 | 0.011392 | 1.02e-06 | 0.00428% | EFF Risk, CFO Other Risk
1418 | FOOTHILL_RAR5227_EOL | 0.86256 | 0.011306 | 0.011306 | 2.15e-05 | 0.00424% | EFF Risk, CFO Other Risk
1419 | ATLANTA_RAR0344_EOL | 2.1832 | 0.011253 | 0.011253 | 1.71e-05 | 0.00422% | CFO Other Risk, EFF Risk
1420 | PASCOE_CB_EOL | 6.4875 | 0.011208 | 0.011205 | 1.44e-05 | 0.00421% | EFF Risk, CFO Other Risk
1421 | CHATTANOOGA_CB_GS1203-1 | 1.796 | 0.011205 | 0.011201 | 1.92e-05 | 0.0042% | EFF Risk, CFO Other Risk
1422 | MENTRY_PME6040-2_EOL | 1.2137 | 0.011194 | 0.011194 | 0.00016648 | 0.0042% | CFO Other Risk, EFF Risk
1423 | SODA SPRINGS_RAR0480_EOL | 16.1171 | 0.011118 | 0.011111 | 9.89e-05 | 0.00417% | EFF Risk, CFO Other Risk
1424 | ROBIN_RCS1249_EOL | 3.2145 | 0.011075 | 0.011074 | 1.67e-06 | 0.00416% | EFF Risk, CFO Other Risk
1425 | SQUINT_RAR0765_EOL | 5.3705 | 0.011065 | 0.011059 | 1.75e-05 | 0.00415% | EFF Risk, CFO Other Risk
1426 | ANGELES_RCS1947_EOL | 3.5067 | 0.011058 | 0.011055 | 1.66e-05 | 0.00415% | EFF Risk, CFO Other Risk
1427 | CHARLIE_RAR0845_EOL | 2.9222 | 0.011045 | 0.011041 | 4.1e-05 | 0.00414% | EFF Risk, CFO Other Risk
1428 | CROWLEY_CB_RCS0285 | 2.5573 | 0.011041 | 0.01104 | 2.15e-06 | 0.00414% | EFF Risk, CFO Other Risk
1429 | VALMONTE_CB_EOL | 2.5727 | 0.011021 | 0.011019 | 3.01e-06 | 0.00414% | EFF Risk, CFO Other Risk
1430 | HOOLIGAN_CB_RCS4059-1 | 2.7138 | 0.011013 | 0.011006 | 2.84e-05 | 0.00413% | EFF Risk, CFO Other Risk
1431 | PALACE_CB_GS7344-1 | 0.66258 | 0.01081 | 0.01081 | 4.29e-06 | 0.00406% | EFF Risk, CFO Other Risk
1432 | SEXTON_RSR3031_RAR7428_PS0020_RCS3033 | 3.2065 | 0.010784 | 0.01078 | 9.29e-05 | 0.00405% | EFF Risk, CFO Other Risk
1433 | INTERIOR_RAR0005_RAR0038 | 3.6486 | 0.01078 | 0.010778 | 3.45e-05 | 0.00405% | EFF Risk, CFO Other Risk
1434 | CANTINA_RCS4443-2_EOL | 0.58522 | 0.010744 | 0.010742 | 3.69e-05 | 0.00403% | EFF Risk, CFO Other Risk
1435 | LANDERS_CB_EOL | 0.25615 | 0.010711 | 0.010711 | 0 | 0.00402% | EFF Risk, CFO Other Risk
1436 | SABRINA_CB_RAR0368_RAR0367_ | 1.574 | 0.010608 | 0.010608 | 1.78e-06 | 0.00398% | EFF Risk, CFO Other Risk
1437 | SODA SPRINGS_RAR0879_EOL | 10.8105 | 0.010606 | 0.010601 | 6.58e-05 | 0.00398% | EFF Risk, CFO Other Risk
1438 | ROCKHILL_RSR4322_RAR1142 | 0.92994 | 0.010524 | 0.010524 | 1.93e-06 | 0.00395% | CFO Other Risk, EFF Risk
1439 | CALGROVE_PS2004_EOL | 0.38202 | 0.010461 | 0.01046 | 4.9e-06 | 0.00393% | CFO Other Risk, EFF Risk
1440 | BOOTLEGGER_RAR4268_EOL | 7.6476 | 0.010449 | 0.010445 | 1.01e-05 | 0.00392% | CFO Other Risk, EFF Risk
1441 | REJADA_CB_RCS0538 | 0.7337 | 0.010342 | 0.010341 | 4.33e-06 | 0.00388% | CFO Other Risk, EFF Risk
1442 | TITAN_RCS5472_EOL | 4.8774 | 0.010299 | 0.010298 | 7.39e-06 | 0.00386% | CFO Other Risk, EFF Risk
1443 | INTERIOR_RAR0038_EOL | 2.9276 | 0.010245 | 0.010244 | 2.76e-05 | 0.00384% | EFF Risk, CFO Other Risk
1444 | ELSTER_RSR0637_RAR0577 | 7.7125 | 0.010221 | 0.010221 | 1.15e-05 | 0.00384% | EFF Risk, CFO Other Risk
1445 | MAYER_RAR7937_EOL | 4.1504 | 0.010102 | 0.010102 | 9.86e-09 | 0.00379% | EFF Risk, CFO Other Risk
1446 | HURST_CB_RAR0317 | 0.51298 | 0.010102 | 0.010101 | 3.33e-06 | 0.00379% | EFF Risk, CFO Other Risk
1447 | PATRIOT_CB_RAR0286 | 1.8503 | 0.010102 | 0.0101 | 3.07e-05 | 0.00379% | EFF Risk, CFO Other Risk
1448 | SALT CREEK_RAR1620_PS0908 | 2.8303 | 0.010076 | 0.010074 | 9.14e-06 | 0.00378% | EFF Risk, CFO Other Risk
1449 | RICARDO_RAR0141_RSR0472 | 2.1698 | 0.010059 | 0.010057 | 3.12e-05 | 0.00377% | EFF Risk, CFO Other Risk
1450 | MORITZ_RCS0372_EOL | 1.7456 | 0.010047 | 0.010044 | 2.54e-05 | 0.00377% | EFF Risk, CFO Other Risk
1451 | PATRICIA_CB_RCS0283_RAR0267_ | 0.37032 | 0.010019 | 0.010019 | 2.96e-06 | 0.00376% | EFF Risk, CFO Other Risk
1452 | ZONE_RCS2381_PS2386_RAR2385_PS2382 | 0.50736 | 0.0099967 | 0.0099966 | 8.68e-07 | 0.00375% | EFF Risk, CFO Other Risk
1453 | TECOLOTE_CB_RSR1573_RCS0046_ | 0.60018 | 0.0099841 | 0.0099754 | 1.7e-05 | 0.00375% | EFF Risk, CFO Other Risk
1454 | FORTRESS_RAR8307_RCS1045 | 0.60054 | 0.0099134 | 0.0099126 | 1.17e-05 | 0.00372% | EFF Risk, CFO Other Risk
1455 | SODA SPRINGS_RAR0538_RCS0505 | 9.2614 | 0.0099077 | 0.009904 | 5.64e-05 | 0.00372% | EFF Risk, CFO Other Risk
1456 | VIOLET_CB_EOL | 4.2361 | 0.0098312 | 0.0098305 | 1.44e-05 | 0.00369% | EFF Risk, CFO Other Risk
1457 | VENWIND 4_CB_EOL | 1.4035 | 0.0098256 | 0.0098256 | 0 | 0.00369% | EFF Risk, CFO Other Risk
1458 | PENSTOCK_PS0641_EOL | 2.4709 | 0.0098122 | 0.0098099 | 7.07e-06 | 0.00368% | CFO Other Risk, EFF Risk
1459 | MORRIE_CB_RCS7714-1 | 0.38588 | 0.0098075 | 0.0098069 | 5e-06 | 0.00368% | EFF Risk, CFO Other Risk
1460 | ACADEMY_CB_RAR8961_RCS0147_PS0376 | 1.2259 | 0.0097803 | 0.0097802 | 4.71e-06 | 0.00367% | EFF Risk, CFO Other Risk
1461 | PICKLE MEADOWS_RAR0156_RCS0269 | 12.6803 | 0.0097738 | 0.0097728 | 7.88e-06 | 0.00367% | EFF Risk, CFO Other Risk
1462 | BOBBIT_RAR8305_EOL | 0.51364 | 0.0097407 | 0.0097406 | 8.46e-07 | 0.00366% | EFF Risk, CFO Other Risk
1463 | ARTIST_CB_RCS5643 | 2.8238 | 0.0097276 | 0.0097234 | 0.00013484 | 0.00365% | CFO Other Risk, EFF Risk
1464 | EQUINOX_CB_RAR7356 | 2.1551 | 0.0097225 | 0.0097224 | 2.27e-06 | 0.00365% | EFF Risk, CFO Other Risk
1465 | JORDAN_RAR0843_EOL | 19.4909 | 0.0096844 | 0.0096838 | 1.02e-05 | 0.00363% | EFF Risk, CFO Other Risk
1466 | SNOW VALLEY_RCS0568_RCS0619 | 1.4648 | 0.0096435 | 0.0096424 | 2.71e-05 | 0.00362% | CFO Other Risk, EFF Risk
1467 | LEON_CB_GS6341-4 | 0.40696 | 0.0096161 | 0.0096155 | 3.7e-05 | 0.00361% | EFF Risk, CFO Other Risk
1468 | NORTH SHORE_RAR0339_EOL | 5.2929 | 0.0095775 | 0.0095624 | 0.00010015 | 0.00359% | EFF Risk, CFO Other Risk
1469 | NATIONS_CB_RCS2254 | 2.2669 | 0.0095623 | 0.0095618 | 2.24e-06 | 0.00359% | EFF Risk, CFO Other Risk
1470 | MCBEAN_CB_RCS0126 | 0.76072 | 0.0095581 | 0.0095574 | 1.64e-05 | 0.00359% | EFF Risk, CFO Other Risk
1471 | LARK_RAR1692_RCS0437 | 2.2541 | 0.0095196 | 0.0095168 | 2.37e-05 | 0.00357% | EFF Risk, CFO Other Risk
1472 | KLEVEN_CB_RCS2491-3 | 0.72929 | 0.0094834 | 0.0094817 | 1.99e-05 | 0.00356% | CFO Other Risk, EFF Risk
1473 | MCCLENNY_CB_EOL | 2.3649 | 0.0094657 | 0.0094656 | 1.07e-06 | 0.00355% | EFF Risk, CFO VEG Risk
1474 | SUTT_552939ET1_EOL | 0.66081 | 0.0094617 | 0.0094608 | 6.14e-06 | 0.00355% | EFF Risk, CFO Other Risk
1475 | FLINTRIDGE_RAR1687_RAR0920 | 1.9268 | 0.0093953 | 0.0093949 | 1.41e-05 | 0.00353% | EFF Risk, CFO Other Risk
1476 | HILLARD_RAR1928_EOL | 2.1629 | 0.0093748 | 0.0093738 | 7.09e-06 | 0.00352% | EFF Risk, CFO Other Risk
1477 | TENNECO_RAR0761_RAR0765_RAR0764_ | 0.42029 | 0.0093171 | 0.0093168 | 3.26e-06 | 0.0035% | EFF Risk, CFO Other Risk
1478 | KEENE_RSR0624_EOL | 1.29 | 0.0092997 | 0.0092991 | 1.19e-06 | 0.00349% | EFF Risk, CFO Other Risk
1479 | TETLEY_RAR0871_RCS0571 | 1.4782 | 0.0092943 | 0.0092922 | 1.07e-05 | 0.00349% | EFF Risk, CFO Other Risk
1480 | BIG CREEK-PORTAL_RCS0002_EOL | 5.313 | 0.0092783 | 0.0092783 | 1.32e-07 | 0.00348% | EFF Risk, CFO Other Risk
1481 | BERMITE_GS7358-1_EOL | 1.2562 | 0.0092618 | 0.0092606 | 2.7e-05 | 0.00348% | EFF Risk, CFO Other Risk
1482 | MAJOR_CB_EOL | 1.6956 | 0.0091986 | 0.0091981 | 7e-06 | 0.00345% | EFF Risk, CFO Other Risk
1483 | DENTAL_RCS0327_EOL | 0.83976 | 0.0091911 | 0.0091908 | 3.45e-06 | 0.00345% | EFF Risk, CFO Other Risk
1484 | ALPINE_RAR0037_EOL | 1.0246 | 0.0091659 | 0.0091653 | 6.54e-06 | 0.00344% | EFF Risk, CFO Other Risk
1485 | KILTS_CB_RCS0803 | 2.7388 | 0.0091283 | 0.0091251 | 3.34e-05 | 0.00343% | EFF Risk, CFO Other Risk
1486 | SAGEHEN_RAR0404_EOL | 6.3735 | 0.0090996 | 0.0090988 | 7.61e-06 | 0.00341% | EFF Risk, CFO Other Risk
1487 | CASEY_CB_RCS9688 | 0.6257 | 0.0090857 | 0.0090852 | 4.49e-07 | 0.00341% | EFF Risk, CFO Other Risk
1488 | KOREA_RAR3597_EOL | 1.1146 | 0.0090847 | 0.0090827 | 1.09e-05 | 0.00341% | EFF Risk, CFO Other Risk
1489 | RACER_BF59341_EOL | 0.2963 | 0.0090794 | 0.0090792 | 5.32e-06 | 0.00341% | EFF Risk, CFO Other Risk
1490 | ERSKINE_RAR0901_EOL | 1.4761 | 0.0090751 | 0.0090742 | 4.83e-06 | 0.00341% | CFO Other Risk, EFF Risk
1491 | LIMBER_CB_GS1029-4 | 0.6868 | 0.0090492 | 0.0090452 | 5.86e-06 | 0.0034% | CFO Other Risk, EFF Risk
1492 | TEMPEST_CB_EOL | 1.587 | 0.0090353 | 0.0090352 | 3.06e-07 | 0.00339% | CFO Other Risk, EFF Risk
1493 | TAMBOURINE_CB_EOL | 0.65373 | 0.0090268 | 0.0090144 | 6.74e-05 | 0.00339% | EFF Risk, CFO Other Risk
1494 | STUTZ_RCS0396_EOL | 3.9254 | 0.0089826 | 0.0089815 | 7.93e-05 | 0.00337% | CFO Other Risk, EFF Risk
1495 | TEJON_PS0887_EOL | 9.4367 | 0.0089195 | 0.0089175 | 1.4e-05 | 0.00335% | EFF Risk, CFO Other Risk
1496 | FLEETWOOD_RAR2567_EOL | 0.71503 | 0.0089017 | 0.0089013 | 3.05e-06 | 0.00334% | EFF Risk, CFO Other Risk
1497 | JUPITER_CB_EOL | 3.9016 | 0.0088704 | 0.0088691 | 5.09e-05 | 0.00333% | EFF Risk, CFO Other Risk
1498 | KEWAMEE_RAR0375_EOL | 1.1759 | 0.0087385 | 0.0087385 | 0.00015301 | 0.00328% | CFO Other Risk, EFF Risk
1499 | BEECHCRAFT_RAR0733_EOL | 1.1043 | 0.0087042 | 0.0087037 | 1.99e-05 | 0.00327% | EFF Risk, CFO Other Risk
1500 | MEDUSA_CB_GS1136-3 | 1.9349 | 0.0086393 | 0.0086391 | 8.75e-06 | 0.00324% | EFF Risk, CFO Other Risk
1501 | HEAPS PEAK_RCS0434_EOL | 1.5281 | 0.0085322 | 0.0085322 | 6.55e-08 | 0.0032% | EFF Risk, CFO Other Risk
1502 | CARVER_RAR0222_RAR0452 | 9.1488 | 0.0085227 | 0.0085226 | 5.67e-06 | 0.0032% | CFO Other Risk, EFF Risk
1503 | CISCO_RAR9600_EOL | 0.61946 | 0.0084057 | 0.0084053 | 4.22e-06 | 0.00315% | EFF Risk, CFO Other Risk
1504 | SEXTON_CB_RAR3032_RSR3031_ | 1.2244 | 0.008371 | 0.0083674 | 3.74e-05 | 0.00314% | EFF Risk, CFO Other Risk
1505 | COACHELLA_RAR0578_EOL | 4.5517 | 0.0083491 | 0.008349 | 3.17e-06 | 0.00313% | EFF Risk, CFO Other Risk
1506 | SEELEY_RAR1081_EOL | 1.3406 | 0.0082997 | 0.0082975 | 8.28e-06 | 0.00311% | EFF Risk, CFO Other Risk
1507 | BURLESON_RCS5704_EOL | 3.617 | 0.0082992 | 0.0082899 | 6.31e-05 | 0.00311% | EFF Risk, CFO Other Risk
1508 | ANTON_RSR5773_EOL | 0.3596 | 0.008278 | 0.0082779 | 1.74e-07 | 0.00311% | EFF Risk, CFO Other Risk
1509 | WELCH_RAR2295_EOL | 6.2625 | 0.0082117 | 0.0082116 | 5.31e-06 | 0.00308% | EFF Risk, CFO Other Risk
1510 | MCLAUGHLIN_RCS0046-1_EOL | 0.29433 | 0.0081711 | 0.0081711 | 3.37e-05 | 0.00307% | EFF Risk, CFO Other Risk
1511 | BENCH_PS1018_EOL | 0.56094 | 0.0081619 | 0.0081617 | 1.37e-06 | 0.00306% | EFF Risk, CFO Other Risk
1512 | RITTER_CB_EOL | 0.95344 | 0.0081536 | 0.0081514 | 1.52e-05 | 0.00306% | CFO Other Risk, EFF Risk
1513 | TIMBER CANYON_CB_RCS1535_RCS1254_ | 2.0974 | 0.0081331 | 0.0081322 | 3.61e-06 | 0.00305% | CFO Other Risk, EFF Risk
1514 | WYLE_CB_RCS4753 | 0.7861 | 0.0081305 | 0.0081288 | 7.97e-06 | 0.00305% | EFF Risk, CFO Other Risk
1515 | SODA SPRINGS_RAR0543_EOL | 13.4956 | 0.0081061 | 0.0081006 | 8.22e-05 | 0.00304% | EFF Risk, CFO Other Risk
1516 | HILTON_RCS0995-1_EOL | 0.42684 | 0.0080928 | 0.0080925 | 8.5e-06 | 0.00304% | CFO Other Risk, EFF Risk
1517 | HI LINE_RCS0035_EOL | 5.9895 | 0.0080913 | 0.0080909 | 2.82e-06 | 0.00304% | EFF Risk, CFO Other Risk
1518 | FULLBACK_RCS1850_EOL | 0.61657 | 0.0080692 | 0.0080691 | 8.68e-06 | 0.00303% | EFF Risk, CFO Other Risk
1519 | ROSEBUD_CB_RAR0282_RAR0279_ | 7.7208 | 0.0080057 | 0.0080046 | 7.12e-06 | 0.003% | CFO Other Risk, EFF Risk
1520 | LITTLE MOUNTAIN_CB_RCS0797_RCS0827_ | 2.697 | 0.0080048 | 0.0080048 | 0 | 0.003% | EFF Risk, CFO Other Risk
1521 | LARK_CB_RAR1692 | 1.5334 | 0.0079834 | 0.0079814 | 1.59e-05 | 0.003% | EFF Risk, CFO Other Risk
1522 | PARCO_CB_RCS2286 | 0.3631 | 0.0079687 | 0.0079657 | 6.61e-06 | 0.00299% | EFF Risk, CFO Other Risk
1523 | RMV 1243_RAR0801_EOL | 1.5038 | 0.0079667 | 0.0079666 | 3.85e-07 | 0.00299% | EFF Risk, CFO Other Risk
1524 | KINSEY_RAR0302_EOL | 6.6872 | 0.007942 | 0.0079413 | 1.94e-06 | 0.00298% | EFF Risk, CFO Other Risk
1525 | KEENE_CB_RAR0786_RSR0624_ | 2.6822 | 0.0078897 | 0.0078891 | 1.9e-06 | 0.00296% | CFO Other Risk, EFF Risk
1526 | JERRY_CB_RCS7752 | 3.5602 | 0.0078893 | 0.0078882 | 2.24e-05 | 0.00296% | EFF Risk, CFO Other Risk
1527 | WHISPER_RAR8325_EOL | 0.27959 | 0.0078441 | 0.0078441 | 3.64e-07 | 0.00294% | EFF Risk, CFO Other Risk
1528 | AGATE_RAR1297_EOL | 0.82573 | 0.0077647 | 0.0077638 | 1.05e-05 | 0.00291% | EFF Risk, CFO Other Risk
1529 | WHIPSTOCK_RSR1302_RAR0145 | 0.30236 | 0.0077623 | 0.0077622 | 1.33e-06 | 0.00291% | CFO Other Risk, EFF Risk
1530 | ALLVIEW_CB_EOL | 2.5791 | 0.0077238 | 0.00772 | 6.59e-05 | 0.0029% | EFF Risk, CFO Other Risk
1531 | FLAGSTAFF_CB_PME9951-4 | 0.73355 | 0.0076856 | 0.0076829 | 6.75e-05 | 0.00288% | EFF Risk, CFO Other Risk
1532 | PENSTOCK_BF76025_EOL | 1.4699 | 0.0076775 | 0.0076758 | 5.99e-06 | 0.00288% | EFF Risk, CFO Other Risk
1533 | BOULDER_PS0241_EOL | 1.7684 | 0.0076492 | 0.0076485 | 1.97e-05 | 0.00287% | EFF Risk, CFO Other Risk
1534 | HONEYWELL_RSR0262_EOL | 2.1637 | 0.0076228 | 0.0076187 | 6.22e-05 | 0.00286% | EFF Risk, CFO Other Risk
1535 | STACK_CB_RCS0685 | 0.37412 | 0.0076146 | 0.0076132 | 6.49e-06 | 0.00286% | EFF Risk, CFO Other Risk
1536 | PINE COVE_PS1668_EOL | 0.78799 | 0.007504 | 0.0075037 | 5e-06 | 0.00282% | EFF Risk, CFO Other Risk
1537 | BACHELOR_CB_RCS0555 | 4.1134 | 0.0074953 | 0.0074944 | 2.8e-05 | 0.00281% | EFF Risk, CFO Other Risk
1538 | WEESHA_PD0219_EOL | 0.81245 | 0.0074426 | 0.0074425 | 1.52e-06 | 0.00279% | EFF Risk, CFO Other Risk
1539 | BADGER_RAR0827_EOL | 1.161 | 0.0074204 | 0.0074183 | 4.92e-05 | 0.00278% | EFF Risk, CFO Other Risk
1540 | TROUT_RCS0190_RCS0369-1 | 1.2055 | 0.0073849 | 0.0073849 | 2.07e-08 | 0.00277% | EFF Risk, CFO Other Risk
1541 | PYLE_CB_RAR1284 | 0.4499 | 0.0073472 | 0.0073437 | 4.14e-06 | 0.00276% | EFF Risk, CFO Other Risk
1542 | PALOMA_PS2349_EOL [2] | 1.0463 | 0.0073385 | 0.0073345 | 9.13e-06 | 0.00275% | EFF Risk, CFO Other Risk
1543 | READY_GS3095-4_EOL | 1.5529 | 0.0072819 | 0.0072772 | 1.19e-05 | 0.00273% | EFF Risk, CFO Other Risk
1544 | CEYLON_CB_GS3087-2 | 0.58669 | 0.0072755 | 0.0072743 | 7.07e-06 | 0.00273% | CFO Other Risk, EFF Risk
1545 | AVENGER_RAR2242_EOL | 1.3216 | 0.0072515 | 0.0072511 | 1.25e-05 | 0.00272% | EFF Risk, CFO Other Risk
1546 | GILLIBRAND_CB_RCS5567-1 | 9.4988 | 0.0072327 | 0.0072084 | 0.00011086 | 0.00271% | EFF Risk, CFO Other Risk
1547 | MORITZ_RAR0364_RAR0652_RAR1218_ | 0.85933 | 0.0071827 | 0.0071814 | 1.16e-05 | 0.0027% | EFF Risk, CFO Other Risk
1548 | TOLA_CB_RCS1466_BF01962_FD03932 | 0.56004 | 0.0071555 | 0.0071546 | 6.54e-06 | 0.00269% | EFF Risk, CFO Other Risk
1549 | MINT CANYON_GS6092B-4_EOL | 1.6516 | 0.0071429 | 0.0071426 | 3.84e-05 | 0.00268% | EFF Risk, CFO Other Risk
1550 | PEACOCK_CB_EOL | 1.0654 | 0.0071324 | 0.0071321 | 4.84e-06 | 0.00268% | EFF Risk, CFO Other Risk
1551 | BECKER_CB_EOL | 0.42461 | 0.0071109 | 0.0071103 | 3.68e-05 | 0.00267% | EFF Risk, CFO Other Risk
1552 | INTERPACE_RCS6462_RAR6470 | 0.26514 | 0.0070311 | 0.0070311 | 1.43e-08 | 0.00264% | EFF Risk, CFO Other Risk
1553 | ERSKINE_CB_RAR0733_RAR0901_ | 0.80687 | 0.0070288 | 0.0070285 | 2.05e-06 | 0.00264% | EFF Risk, CFO Other Risk
1554 | AMBERSKY_CB_EOL | 2.4307 | 0.0070017 | 0.0069988 | 5.98e-05 | 0.00263% | EFF Risk, CFO Other Risk
1555 | BALCOM_CB_RAR0085 | 1.1457 | 0.0069284 | 0.006923 | 8.8e-06 | 0.0026% | EFF Risk, CFO Other Risk
1556 | PICKENS_CB_EOL | 0.68027 | 0.0069257 | 0.0069189 | 1.17e-05 | 0.0026% | EFF Risk, CFO Other Risk
1557 | CANAL_RCS1709_PS1016 | 1.472 | 0.0069219 | 0.0069219 | 9.72e-09 | 0.0026% | EFF Risk, CFO Other Risk
1558 | YOSEMITE_GS1788-3_RCS6315 | 0.79278 | 0.0068985 | 0.0068951 | 1.14e-05 | 0.00259% | EFF Risk, CFO Other Risk
1559 | JORDAN_RAR0846_RAR0843_RAR0844_ | 9.8345 | 0.0068836 | 0.0068833 | 5.15e-06 | 0.00258% | EFF Risk, CFO Other Risk
1560 | JENKS LAKE_RCS0504_EOL | 3.7929 | 0.0068644 | 0.006864 | 5.89e-06 | 0.00258% | EFF Risk, CFO Other Risk
1561 | LEONA_CB_RCS3527 | 2.9529 | 0.0068386 | 0.0068209 | 6.51e-05 | 0.00257% | CFO Other Risk, EFF Risk
1562 | BUNDY_RAR9180_EOL | 0.4163 | 0.0068268 | 0.0068265 | 4.47e-06 | 0.00256% | EFF Risk, CFO Other Risk
1563 | OSLO_RCS6903-2_EOL | 2.0354 | 0.0067541 | 0.0067541 | 0.00015725 | 0.00253% | EFF Risk, CFO Other Risk
1564 | LEXINGTON_CB_EOL | 1.7958 | 0.0067382 | 0.0067368 | 1.24e-05 | 0.00253% | EFF Risk, CFO Other Risk
1565 | ANGUS_RAR3737_EOL | 2.3516 | 0.0066345 | 0.006629 | 2.91e-05 | 0.00249% | EFF Risk, CFO Other Risk
1566 | OLYMPIAD_RCS1718-2_RCS7025-3 | 0.38903 | 0.0066256 | 0.0066211 | 4.41e-05 | 0.00249% | EFF Risk, CFO Other Risk
1567 | JENKS LAKE_CB_PS0502 | 0.89688 | 0.0066137 | 0.0066136 | 1.14e-06 | 0.00248% | EFF Risk, CFO Other Risk
1568 | TULLY_CB_RCS1000 | 2.5118 | 0.0065977 | 0.0065968 | 3.2e-05 | 0.00248% | EFF Risk, CFO Other Risk
1569 | CATARACT_GS4197-4_RCS3798 | 0.98105 | 0.00659 | 0.006588 | 2.84e-06 | 0.00247% | CFO Other Risk, EFF Risk
1570 | LARK_RCS0437_EOL | 2.5014 | 0.0065714 | 0.0065683 | 2.6e-05 | 0.00247% | EFF Risk, CFO Other Risk
1571 | LESSER_CB_PS0294 | 0.42371 | 0.0065454 | 0.0065453 | 1.22e-06 | 0.00246% | EFF Risk, CFO Other Risk
1572 | ERIN_RCS0290_EOL | 2.9396 | 0.006538 | 0.0065361 | 2.47e-05 | 0.00245% | EFF Risk, CFO Other Risk
1573 | KIRBY_PS8184_EOL | 0.88389 | 0.0065276 | 0.0065273 | 6.91e-06 | 0.00245% | EFF Risk, CFO Other Risk
1574 | DEALER_RAR0262_PS1003 | 2.1612 | 0.0065208 | 0.0065195 | 1.48e-05 | 0.00245% | EFF Risk, CFO Other Risk
1575 | PADOVA_PS3065_RCS0065 | 0.45968 | 0.0064821 | 0.0064811 | 7.6e-06 | 0.00243% | EFF Risk, CFO Other Risk
1576 | PLAYER_RCS0407_EOL | 0.89783 | 0.0064797 | 0.0064797 | 7.8e-10 | 0.00243% | EFF Risk, CFO Other Risk
1577 | TURNPIKE_RCS0074_RCS0355 | 2.3196 | 0.0064533 | 0.0064399 | 3.6e-05 | 0.00242% | EFF Risk, CFO Other Risk
1578 | SKYLAND_RAR0882_RAR0775 | 1.0055 | 0.0064515 | 0.0064502 | 6.26e-06 | 0.00242% | EFF Risk, CFO Other Risk
1579 | BIDDER_CB_RCS5163_RCS0303_ | 2.5274 | 0.0064317 | 0.0064312 | 8.54e-07 | 0.00241% | EFF Risk, CFO Other Risk
1580 | LINEBACKER_GS5942-4_EOL | 0.54528 | 0.0064303 | 0.0064291 | 5.35e-05 | 0.00241% | EFF Risk, CFO Other Risk
1581 | VULCAN_CB_EOL | 0.2844 | 0.0063525 | 0.0063525 | 1.59e-07 | 0.00238% | EFF Risk, CFO Other Risk
1582 | YOSEMITE_BF35210_EOL | 0.25968 | 0.0063242 | 0.0063234 | 3.48e-06 | 0.00237% | EFF Risk, CFO Other Risk
1583 | RED MOUNTAIN_PS0094_RCS0681 | 3.4672 | 0.0062909 | 0.0062894 | 4.31e-06 | 0.00236% | EFF Risk, CFO Other Risk
1584 | POWELL_CB_EOL | 3.1373 | 0.0062881 | 0.0062873 | 8.64e-05 | 0.00236% | EFF Risk, CFO Other Risk
1585 | AGNEW_CB_EOL | 0.46742 | 0.0062678 | 0.0062678 | 4.6e-08 | 0.00235% | EFF Risk, CFO Other Risk
1586 | CORNWALL_CB_RCS1063 | 1.8641 | 0.0062652 | 0.0062645 | 6.29e-05 | 0.00235% | EFF Risk, CFO Other Risk
1587 | JORDAN_RAR0075_EOL | 23.9269 | 0.0062622 | 0.0062615 | 1.26e-05 | 0.00235% | EFF Risk, CFO Other Risk
1588 | SAWPIT_CB_EOL | 2.8245 | 0.0062482 | 0.0062482 | 0 | 0.00234% | EFF Risk, CFO Other Risk
1589 | LATTE_RAR1037_EOL | 0.90866 | 0.0062429 | 0.0062429 | 1.78e-06 | 0.00234% | EFF Risk, CFO Other Risk
1590 | HILLCREST_RCS0107_EOL | 7.2972 | 0.0062277 | 0.0062246 | 8.42e-05 | 0.00234% | EFF Risk, CFO Other Risk
1591 | HARNAGE_GS8572-3_RAR0618 | 0.9559 | 0.0061755 | 0.0061755 | 3.4e-06 | 0.00232% | EFF Risk, CFO Other Risk
1592 | PREDATOR_CB_EOL | 2.3822 | 0.006128 | 0.0061267 | 2.56e-05 | 0.0023% | EFF Risk, CFO Other Risk
1593 | FRONTIER_GS8591-2_EOL | 0.36389 | 0.0060767 | 0.0060763 | 1.75e-05 | 0.00228% | EFF Risk, CFO Other Risk
1594 | MAXSON_RAR1580_EOL | 1.7351 | 0.0060589 | 0.0060436 | 4.66e-05 | 0.00227% | EFF Risk, CFO Other Risk
1595 | PANCAKE_CB_EOL | 1.1874 | 0.0060556 | 0.0060554 | 8.64e-06 | 0.00227% | EFF Risk, CFO Other Risk
1596 | SEXTON_RCS3033_EOL | 1.3787 | 0.006027 | 0.0060244 | 4.04e-05 | 0.00226% | EFF Risk, CFO Other Risk
1597 | SODA SPRINGS_RAR0873_RAR0543_RCS0541_ | 6.6048 | 0.0060235 | 0.0060208 | 4.09e-05 | 0.00226% | EFF Risk, CFO Other Risk
1598 | CACTUS_CB_EOL | 0.88049 | 0.0059386 | 0.0059386 | 1.6e-07 | 0.00223% | EFF Risk, CFO Other Risk
1599 | MORGANSTEIN_RCS0506_EOL | 0.80199 | 0.0059357 | 0.0059354 | 1.06e-05 | 0.00223% | CFO Other Risk, EFF Risk
1600 | PAR_CB_EOL | 0.29316 | 0.0059281 | 0.005928 | 1.71e-07 | 0.00222% | EFF Risk, CFO Other Risk
1601 | DOROF_RAR9168_EOL | 0.52236 | 0.0059083 | 0.0059081 | 1.45e-05 | 0.00222% | CFO Other Risk, EFF Risk
1602 | HI LINE_CB_RAR0059 | 2.7352 | 0.0058893 | 0.0058888 | 1.61e-06 | 0.00221% | EFF Risk, CFO Other Risk
1603 | JADE_RCS5438-3_EOL | 0.69397 | 0.0058814 | 0.005881 | 5.75e-05 | 0.00221% | CFO Other Risk, EFF Risk
1604 | PAYNE_RCS0186_RAR0962_RAR0963_ | 1.027 | 0.0058551 | 0.0058535 | 1.05e-05 | 0.0022% | EFF Risk, CFO Other Risk
1605 | WEESHA_PS0244_EOL | 1.1549 | 0.0058117 | 0.0058112 | 2.45e-06 | 0.00218% | EFF Risk, CFO Other Risk
1606 | SAUTERNE_RSR2096_EOL | 0.31884 | 0.0057873 | 0.005786 | 6.19e-06 | 0.00217% | CFO Other Risk, EFF Risk
1607 | FLINTRIDGE_RAR0920_EOL | 2.4678 | 0.005779 | 0.005778 | 1.88e-05 | 0.00217% | EFF Risk, CFO Other Risk
1608 | BELPAC_CB_GS8076-5 | 0.35653 | 0.0057275 | 0.0057229 | 1.52e-05 | 0.00215% | EFF Risk, CFO Other Risk
1609 | CORNWALL_RAR1089_EOL | 0.55059 | 0.0056318 | 0.0056317 | 1.85e-05 | 0.00211% | EFF Risk, CFO Other Risk
1610 | CASSIDY_RCS1246-2_GS1054-4 | 1.2855 | 0.0055958 | 0.0055932 | 3.15e-05 | 0.0021% | EFF Risk, CFO Other Risk
1611 | TWISTER_RAR6337_EOL | 0.84579 | 0.0055516 | 0.0055514 | 2.6e-06 | 0.00208% | CFO Other Risk, EFF Risk
1612 | BOBSLED_RCS0059_EOL | 1.2019 | 0.0055431 | 0.0055273 | 6.5e-05 | 0.00208% | EFF Risk, CFO Other Risk
1613 | SALT CREEK_PS0908_EOL | 4.6454 | 0.0054877 | 0.005487 | 1.11e-05 | 0.00206% | EFF Risk, CFO Other Risk
1614 | ELECTRA_CB_GS7901-2 | 1.126 | 0.0054694 | 0.0054683 | 6.9e-06 | 0.00205% | CFO Other Risk, EFF Risk
1615 | DONLON_RAR3474_EOL | 0.35504 | 0.0054579 | 0.0054577 | 1.01e-06 | 0.00205% | EFF Risk, CFO Other Risk
1616 | HORTON_CB_RCS1244-3 | 0.39657 | 0.0053942 | 0.0053935 | 2.9e-05 | 0.00202% | CFO Other Risk, EFF Risk
1617 | CONCEPCION_CB_RCS1606 | 4.921 | 0.0053722 | 0.0053708 | 6.95e-06 | 0.00202% | EFF Risk, CFO Other Risk
1618 | PICKLE MEADOWS_RCS0269_EOL | 3.1388 | 0.0053621 | 0.0053618 | 2.11e-06 | 0.00201% | EFF Risk, CFO Other Risk
1619 | ANACONDA_RCS0119_EOL | 0.46183 | 0.0053348 | 0.0053323 | 2.26e-05 | 0.002% | EFF Risk, CFO Other Risk
1620 | SCIURBA_RCS1117_RCS1122 | 2.4334 | 0.0053218 | 0.005321 | 6.61e-05 | 0.002% | EFF Risk, CFO Other Risk
1621 | INTAKE_RCS0617_RAR0785 | 10.2832 | 0.0052921 | 0.0052915 | 5.75e-06 | 0.00199% | EFF Risk, CFO Other Risk
1622 | CUTHBERT_BF35584_EOL | 0.46021 | 0.0052741 | 0.005273 | 6.77e-06 | 0.00198% | CFO Other Risk, EFF Risk
1623 | WEIRICK_CB_RCS0656 | 0.56582 | 0.0052626 | 0.0052621 | 4.55e-06 | 0.00197% | EFF Risk, CFO Other Risk
1624 | HURLEY_CB_RCS0123 | 3.5067 | 0.0052568 | 0.0052506 | 2.11e-05 | 0.00197% | EFF Risk, CFO Other Risk
1625 | CONCEPCION_RCS1606_RAR0612 | 4.8496 | 0.0052325 | 0.0052276 | 1.04e-05 | 0.00196% | EFF Risk, CFO Other Risk
1626 | BARRINGTON_CB_RAR7346_RAR1187_ | 0.72857 | 0.0052034 | 0.0052019 | 1.97e-06 | 0.00195% | EFF Risk, CFO Other Risk
1627 | TUFA_RAR0289_EOL | 15.5127 | 0.005186 | 0.0051843 | 1.05e-05 | 0.00195% | EFF Risk, CFO Other Risk
1628 | STAGHORN_GS5793-2_EOL | 0.25629 | 0.0051638 | 0.0051627 | 2.98e-06 | 0.00194% | EFF Risk, CFO Other Risk
1629 | GARDEN_PS6644_EOL | 2.2365 | 0.0051604 | 0.0051564 | 2.05e-05 | 0.00194% | EFF Risk, CFO Other Risk
1630 | DINKEY CREEK_CB_EOL | 5.9411 | 0.0051473 | 0.0051471 | 1.17e-06 | 0.00193% | EFF Risk, CFO Other Risk
1631 | BALLOON_CB_RAR1061 | 0.59996 | 0.0051258 | 0.0051235 | 1.11e-05 | 0.00192% | EFF Risk, CFO Other Risk
1632 | CONCEPCION_RAR2129_EOL | 14.0041 | 0.0051131 | 0.0051095 | 1.94e-05 | 0.00192% | EFF Risk, CFO Other Risk
1633 | RAISIN_RCS0346_EOL | 2.4166 | 0.0050492 | 0.0050469 | 0.00022515 | 0.00189% | EFF Risk, CFO Other Risk
1634 | LIMITED_CB_RCS1108 | 1.581 | 0.0050444 | 0.0050393 | 3.87e-05 | 0.00189% | EFF Risk, CFO Other Risk
1635 | ROTEC_RCS1528_RAR7372_RCS1527_PME5300-3 | 0.61073 | 0.0050438 | 0.0050428 | 3.66e-06 | 0.00189% | CFO Other Risk, EFF Risk
1636 | ELAINE_CB_EOL | 0.59939 | 0.0050381 | 0.005038 | 1.08e-06 | 0.00189% | EFF Risk, CFO Other Risk
1637 | ROYCE_CB_EOL | 0.38299 | 0.0050046 | 0.0050046 | 0 | 0.00188% | EFF Risk, CFO Other Risk
1638 | GRAPEFRUIT_RCS0186_EOL | 0.60906 | 0.0050022 | 0.0050012 | 7.85e-06 | 0.00188% | EFF Risk, CFO Other Risk
1639 | VENGEANCE_RAR8731_EOL | 0.74536 | 0.0049819 | 0.0049818 | 1.62e-05 | 0.00187% | EFF Risk, CFO Other Risk
1640 | STRATHERN_RSR0412_RAR5083_RCS1764-4_ | 0.63399 | 0.0049407 | 0.0049384 | 1.14e-05 | 0.00185% | CFO Other Risk, EFF Risk
1641 | BIGFOOT_CB_EOL | 1.8435 | 0.004898 | 0.0048979 | 1.19e-06 | 0.00184% | EFF Risk, CFO Other Risk
1642 | LOWELL_CB_RAR0980 | 2.109 | 0.0048704 | 0.0048695 | 1.69e-05 | 0.00183% | EFF Risk, CFO Other Risk
1643 | GRENADE_CB_GS5166-2 | 0.57907 | 0.0048026 | 0.0048016 | 1.64e-06 | 0.0018% | EFF Risk, CFO Other Risk
1644 | JORDAN_RAR0849_RAR0099_RAR0841_ | 20.8719 | 0.0047923 | 0.0047917 | 1.09e-05 | 0.0018% | EFF Risk, CFO Other Risk
1645 | SHIPLEY_RAR9228_EOL | 1.1946 | 0.0047801 | 0.0047801 | 1e-05 | 0.00179% | EFF Risk, CFO Other Risk
1646 | TEJON_RCS1309_EOL | 5.3207 | 0.004755 | 0.0047535 | 8.25e-06 | 0.00178% | EFF Risk, CFO Other Risk
1647 | SUGARLOAF_CB_EOL | 4.9566 | 0.0047365 | 0.0047355 | 4.03e-06 | 0.00178% | EFF Risk, CFO VEG Risk
1648 | SPLENDOR_GS1026-2_EOL | 0.97598 | 0.0046352 | 0.0046343 | 0.00017376 | 0.00174% | EFF Risk, CFO Other Risk
1649 | NORTHPARK_RCS1998-1_EOL | 1.9691 | 0.0045956 | 0.0045946 | 1.85e-05 | 0.00172% | EFF Risk, CFO Other Risk
1650 | LAMANDA_CB_RCS1836 [2] | 0.55277 | 0.0045566 | 0.0045544 | 6.62e-06 | 0.00171% | EFF Risk, CFO Other Risk
1651 | RED MOUNTAIN_RAR0046_EOL | 4.3989 | 0.0044513 | 0.0044502 | 4.73e-06 | 0.00167% | EFF Risk, CFO Other Risk
1652 | HILLARD_CB_RAR1928 | 1.5715 | 0.0044422 | 0.004441 | 5.64e-06 | 0.00167% | EFF Risk, CFO Other Risk
1653 | VENGEANCE_PS0229_PS0492 | 0.59778 | 0.0044188 | 0.0044187 | 1.3e-05 | 0.00166% | EFF Risk, CFO Other Risk
1654 | TRAM_RCS0411_EOL | 3.0312 | 0.0044187 | 0.0044186 | 4.7e-06 | 0.00166% | EFF Risk, CFO Other Risk
1655 | SLALOM_GS0004-4_EOL | 0.95705 | 0.0043764 | 0.0043661 | 8.1e-05 | 0.00164% | EFF Risk, CFO Other Risk
1656 | GRANDAD_RAR0051_EOL | 5.5572 | 0.0043288 | 0.0043286 | 9.08e-07 | 0.00162% | EFF Risk, CFO Other Risk
1657 | WINTHROP_CB_EOL | 0.28283 | 0.0042807 | 0.0042793 | 2.28e-05 | 0.00161% | EFF Risk, CFO Other Risk
1658 | SKINKLE_PS0275_EOL | 1.2429 | 0.0042639 | 0.0042638 | 2.32e-07 | 0.0016% | EFF Risk, CFO Other Risk
1659 | CONWAY_CB_RAR0222 | 4.0156 | 0.0041851 | 0.004185 | 4.38e-07 | 0.00157% | EFF Risk, CFO Other Risk
1660 | CABANA_CB_RCS6762 | 0.9259 | 0.0041829 | 0.0041752 | 0.00011577 | 0.00157% | EFF Risk, CFO Other Risk
1661 | JORDAN_RSR0500_RAR0846_RAR0106_ | 2.5856 | 0.0041592 | 0.0041591 | 1.35e-06 | 0.00156% | EFF Risk, CFO Other Risk
1662 | MIDDLE ROAD_BF39088_EOL | 0.59516 | 0.0041411 | 0.0041409 | 9.22e-07 | 0.00155% | EFF Risk, CFO Other Risk
1663 | CAMPBELL_RAR3935_EOL | 2.2665 | 0.0040861 | 0.0040859 | 5.61e-06 | 0.00153% | EFF Risk, CFO Other Risk
1664 | AUBURN_RAR0463_EOL | 1.0044 | 0.0040668 | 0.0040667 | 1.66e-05 | 0.00153% | EFF Risk, CFO Other Risk
1665 | DONLON_RAR0231_EOL | 0.64579 | 0.0040665 | 0.0040661 | 1.93e-06 | 0.00153% | EFF Risk, CFO Other Risk
1666 | SAN NICHOLAS_RCS0025_RAR0753 | 0.96106 | 0.0040586 | 0.0040552 | 3.36e-05 | 0.00152% | EFF Risk, CFO Other Risk
1667 | GUSHER_CB_PS0519 | 1.797 | 0.0039937 | 0.0039929 | 1.57e-05 | 0.0015% | EFF Risk, CFO Other Risk
1668 | PERIMETER_RAR0468_RAR0835 | 2.2975 | 0.0039449 | 0.0039433 | 1.38e-05 | 0.00148% | EFF Risk, CFO Other Risk
1669 | YORKTOWN_RCS0827_EOL | 1.9589 | 0.0039229 | 0.0039224 | 1.34e-05 | 0.00147% | EFF Risk, CFO Other Risk
1670 | MIST_RAR0392_EOL | 1.8547 | 0.00392 | 0.0039188 | 1.87e-06 | 0.00147% | CFO Other Risk, EFF Risk
1671 | RIM_RCS0306_EOL | 0.9453 | 0.0038749 | 0.0038732 | 1.57e-05 | 0.00145% | EFF Risk, CFO Other Risk
1672 | FELDSPAR_GS4867-3_EOL | 3.6705 | 0.0038594 | 0.0038594 | 5.37e-05 | 0.00145% | EFF Risk, CFO Other Risk
1673 | NAPA_RCS0241_EOL | 1.8118 | 0.0038021 | 0.0038015 | 9.38e-06 | 0.00143% | EFF Risk, CFO Other Risk
1674 | LARCH_RCS3120_EOL | 2.2497 | 0.0037992 | 0.0037992 | 5.27e-07 | 0.00143% | EFF Risk, CFO Other Risk
1675 | ROBIN_BF73573_EOL | 0.72559 | 0.003778 | 0.0037777 | 4.82e-07 | 0.00142% | CFO Other Risk, EFF Risk
1676 | TERRA COTTA_RCS8583_RCS1888 | 1.3469 | 0.0037766 | 0.0037766 | 5.73e-08 | 0.00142% | EFF Risk, CFO Other Risk
1677 | LAWMAN_RCS0595_RSR6128 | 1.6636 | 0.0037707 | 0.0037683 | 1.5e-05 | 0.00141% | EFF Risk, CFO Other Risk
1678 | LA VACA_CB_RCS0321 | 0.62891 | 0.0037577 | 0.0037532 | 5.32e-05 | 0.00141% | EFF Risk, CFO Other Risk
1679 | NEPAL_CB_RAR0320 | 0.33548 | 0.0037429 | 0.003737 | 6.2e-06 | 0.0014% | CFO Other Risk, EFF Risk
1680 | INTERIOR_RSR0014_BS3532-L | 1.1687 | 0.0037317 | 0.0037312 | 1.1e-05 | 0.0014% | EFF Risk, CFO Other Risk
1681 | KINSEY_RAR5737_PS0719 | 2.9835 | 0.0037245 | 0.0037242 | 8.63e-07 | 0.0014% | EFF Risk, CFO Other Risk
1682 | MIST_CB_RAR3857_RAR0306_ | 2.098 | 0.0037152 | 0.0037147 | 1.22e-06 | 0.00139% | EFF Risk, CFO Other Risk
1683 | WRIGLEY_CB_EOL | 0.8084 | 0.0037094 | 0.0037063 | 2.35e-05 | 0.00139% | EFF Risk, CFO Other Risk
1684 | CLARINET_RAR0297_EOL | 1.7503 | 0.0037041 | 0.0036996 | 1.17e-05 | 0.00139% | EFF Risk, CFO Other Risk
1685 | RESORT_RCS8679_EOL | 3.0484 | 0.0037028 | 0.0037028 | 4.46e-08 | 0.00139% | EFF Risk, CFO Other Risk
1686 | CROFT_RCS0764-2_EOL | 1.9505 | 0.0036965 | 0.0036931 | 3.89e-05 | 0.00139% | EFF Risk, CFO Other Risk
1687 | NERO_PS0401_RCS0097 | 0.59301 | 0.0036956 | 0.0036949 | 6.33e-06 | 0.00139% | EFF Risk, CFO Other Risk
1688 | BIRCHIM_RAR0223_EOL | 3.0255 | 0.0036753 | 0.0036743 | 3.72e-06 | 0.00138% | CFO Other Risk, EFF Risk
1689 | MAGIC_CB_EOL | 0.25275 | 0.0036619 | 0.0036614 | 1.75e-05 | 0.00137% | EFF Risk, CFO Other Risk
1690 | JOHNSONDALE_CB_EOL | 2.0317 | 0.0036503 | 0.0036503 | 2.88e-07 | 0.00137% | EFF Risk, CFO Other Risk
1691 | LIMONITE_RCS0668_EOL | 0.54728 | 0.0036493 | 0.0036493 | 1.6e-08 | 0.00137% | EFF Risk, CFO Other Risk
1692 | JARVIS_PS4129_EOL | 1.368 | 0.003649 | 0.0036487 | 3.42e-06 | 0.00137% | EFF Risk, CFO Other Risk
1693 | MONACHE_RAR4242_EOL | 0.41967 | 0.0036485 | 0.0036485 | 7.22e-06 | 0.00137% | EFF Risk, CFO Other Risk
1694 | CANEBRAKE_RAR0909_EOL | 4.767 | 0.0036358 | 0.0036346 | 4.01e-06 | 0.00136% | EFF Risk, CFO Other Risk
1695 | HOSPAT_RCS0713_GS1492-3 | 0.53539 | 0.0036334 | 0.0036332 | 2.86e-06 | 0.00136% | EFF Risk, CFO Other Risk
1696 | RESORT_RCS7326_RAR1012 | 2.0753 | 0.0036253 | 0.0036253 | 6.58e-08 | 0.00136% | CFO Other Risk, EFF Risk
1697 | WHITECLIFF_RCS5930-4_EOL | 0.47844 | 0.0036243 | 0.0036233 | 7.34e-06 | 0.00136% | EFF Risk, CFO Other Risk
1698 | FRISBIE_RAR6579_EOL | 0.54699 | 0.0036218 | 0.0036212 | 7.18e-06 | 0.00136% | EFF Risk, CFO Other Risk
1699 | CHELLA_RSR5721_EOL | 0.88236 | 0.0036174 | 0.0036171 | 9.09e-06 | 0.00136% | CFO Other Risk, EFF Risk
1700 | TALLEY_CB_GS0506-4 | 3.4076 | 0.0036112 | 0.0036038 | 0.00012233 | 0.00136% | EFF Risk, CFO Other Risk
1701 | SANCHO_CB_EOL | 1.4442 | 0.003594 | 0.0035939 | 4.53e-07 | 0.00135% | EFF Risk, CFO Other Risk
1702 | POTTERY_CB_RCS0654 | 1.4044 | 0.0035836 | 0.003583 | 6.24e-06 | 0.00134% | EFF Risk, CFO Other Risk
1703 | KINSEY_RCS0708_RAR5737 | 5.9958 | 0.0035693 | 0.0035686 | 1.74e-06 | 0.00134% | EFF Risk, CFO Other Risk
1704 | HEMACINTO_RCS0252_EOL | 0.4428 | 0.0035633 | 0.0035629 | 6.89e-06 | 0.00134% | CFO Other Risk, EFF Risk
1705 | SORRENTO_CB_EOL | 0.40982 | 0.003559 | 0.0035582 | 1.14e-05 | 0.00134% | EFF Risk, CFO Other Risk
1706 | TUBA_RCS0333_EOL [4] | 2.636 | 0.0035378 | 0.0035349 | 5e-05 | 0.00133% | EFF Risk, CFO Other Risk
1707 | AVENGER_RAR2241_EOL | 2.2994 | 0.0035377 | 0.003537 | 2.15e-05 | 0.00133% | EFF Risk, CFO Other Risk
1708 | JORDAN_RAR0106_RAR0075 | 16.3923 | 0.0035053 | 0.0035048 | 8.58e-06 | 0.00132% | EFF Risk, CFO Other Risk
1709 | TREVINO_CB_GS0433-3 | 0.58674 | 0.0035036 | 0.0035036 | 0 | 0.00131% | EFF Risk, CFO Other Risk
1710 | CARLET_CB_RAR0623_RSR7957_ | 0.49107 | 0.0034976 | 0.0034963 | 5.65e-06 | 0.00131% | EFF Risk, CFO Other Risk
1711 | COJO_CB_EOL | 5.1954 | 0.0034945 | 0.0034942 | 9.97e-07 | 0.00131% | EFF Risk, CFO Other Risk
1712 | DYNAMO_CB_RAR0225 | 3.8046 | 0.0034935 | 0.0034935 | 1.26e-07 | 0.00131% | EFF Risk, CFO Other Risk
1713 | TROUT_CB_RCS0190 | 0.68667 | 0.0034852 | 0.0034852 | 5.32e-09 | 0.00131% | EFF Risk, CFO Other Risk
1714 | STEEL_CB_RCS0218 | 1.7786 | 0.0034831 | 0.0034829 | 1.29e-06 | 0.00131% | CFO Other Risk, EFF Risk
1715 | PERIMETER_RAR0835_EOL | 2.876 | 0.0034702 | 0.0034687 | 1.67e-05 | 0.0013% | EFF Risk, CFO Other Risk
1716 | BIRCHIM_RAR0323_EOL | 10.8169 | 0.0034564 | 0.0034536 | 1.26e-05 | 0.0013% | EFF Risk, CFO Other Risk
1717 | KINSEY_RAR0452_EOL | 2.9724 | 0.0034369 | 0.0034366 | 8.6e-07 | 0.00129% | EFF Risk, CFO Other Risk
1718 | ACADEMY_PS0376_EOL | 0.3118 | 0.0034144 | 0.0034144 | 1.2e-06 | 0.00128% | EFF Risk, CFO Other Risk
1719 | CAESAR_CB_RCS0610 | 1.2623 | 0.0033721 | 0.0033694 | 3.92e-06 | 0.00127% | CFO Other Risk, EFF Risk
1720 | BOULDER_GS0961-3_EOL | 0.43415 | 0.0033621 | 0.0033583 | 8.5e-06 | 0.00126% | EFF Risk, CFO Other Risk
1721 | ROSEMONT_RCS0623_EOL | 6.7418 | 0.0033164 | 0.0033115 | 2.37e-05 | 0.00124% | EFF Risk, CFO Other Risk
1722 | SAINT JO_CB_RSR0028 | 1.8409 | 0.0033052 | 0.0033007 | 7.1e-05 | 0.00124% | EFF Risk, CFO Other Risk
1723 | ROADRUNNER_CB_PS0728 | 0.5246 | 0.0032855 | 0.0032851 | 3.2e-06 | 0.00123% | EFF Risk, CFO Other Risk
1724 | RED MOUNTAIN_RCS0681_RAR0046 | 1.7369 | 0.00328 | 0.0032797 | 1.84e-06 | 0.00123% | EFF Risk, CFO Other Risk
1725 | THORNTON_RCS0144_EOL | 0.30445 | 0.0032488 | 0.0032476 | 5.68e-06 | 0.00122% | EFF Risk, CFO Other Risk
1726 | SEBASTIAN_RAR5735_EOL | 0.79292 | 0.0032057 | 0.0032052 | 1.14e-05 | 0.0012% | EFF Risk, CFO Other Risk
1727 | SNOW VALLEY_RCS0619_EOL | 1.8867 | 0.0031932 | 0.0031918 | 3.49e-05 | 0.0012% | CFO Other Risk, EFF Risk
1728 | MORITZ_RCS0590_RAR1064_RCS0372_ | 0.86805 | 0.0031581 | 0.0031566 | 1.26e-05 | 0.00119% | EFF Risk, CFO Other Risk
1729 | COOLEY_CB_PS0042 | 1.4937 | 0.0031527 | 0.0031522 | 3.47e-05 | 0.00118% | EFF Risk, CFO Other Risk
1730 | BLACKHILLS_BF34119_EOL | 0.25149 | 0.0031464 | 0.0031461 | 7.76e-06 | 0.00118% | EFF Risk, CFO Other Risk
1731 | STEVENSON_RAR0253_EOL | 12.3755 | 0.0031377 | 0.0031375 | 1.07e-06 | 0.00118% | EFF Risk, CFO Other Risk
1732 | COVEVIEW_RCS6584-4_EOL | 1.6781 | 0.0031307 | 0.0031288 | 0.00031861 | 0.00117% | EFF Risk, CFO Other Risk
1733 | LIVERMORE_RCS0323_EOL | 1.8983 | 0.0031304 | 0.0031302 | 1.44e-05 | 0.00117% | EFF Risk, CFO Other Risk
1734 | KILTS_RCS0803_EOL | 0.50762 | 0.0031173 | 0.0031165 | 6.37e-06 | 0.00117% | EFF Risk, CFO Other Risk
1735 | EBERT_CB_RCS2489-4 | 0.57236 | 0.003104 | 0.0031037 | 4.04e-06 | 0.00116% | CFO Other Risk, EFF Risk
1736 | AVENGER_CB_RCS2240 | 1.0636 | 0.0030984 | 0.0030981 | 9.9e-06 | 0.00116% | EFF Risk, CFO Other Risk
1737 | CRESTWIND_CB_EOL | 2.8948 | 0.0030832 | 0.0030826 | 3.27e-05 | 0.00116% | EFF Risk, CFO Other Risk
1738 | CAL POLY_GS3035-4_EOL | 0.53425 | 0.0030732 | 0.0030724 | 9.86e-06 | 0.00115% | EFF Risk, CFO Other Risk
1739 | JARVIS_RAR0991_RAR0993_RAR0992_ | 2.3044 | 0.0030441 | 0.0030436 | 6.14e-06 | 0.00114% | CFO Other Risk, EFF Risk
1740 | HASKELL_RCS1897_RAR4203 | 2.3468 | 0.0030349 | 0.0030335 | 0.00010805 | 0.00114% | EFF Risk, CFO Other Risk
1741 | SCIURBA_RAR1490_RCS1117 | 0.7072 | 0.0030264 | 0.0030261 | 1.94e-05 | 0.00114% | EFF Risk, CFO Other Risk
1742 | BADGER_RCS4207-3_RAR0827_GS1114-3_ | 0.48831 | 0.0030242 | 0.0030222 | 2.18e-05 | 0.00113% | CFO Other Risk, EFF Risk
1743 | NUBIA_RCS4138-1_EOL | 0.59462 | 0.0030154 | 0.0030149 | 1.48e-05 | 0.00113% | EFF Risk, CFO Other Risk
1744 | ROI-TAN_PS0556_PS1167 | 1.0409 | 0.0029846 | 0.0029824 | 4.39e-05 | 0.00112% | EFF Risk, CFO Other Risk
1745 | MORELAND_RCS1015-1_RAR1389 | 2.5945 | 0.0029807 | 0.0029747 | 3.8e-05 | 0.00112% | EFF Risk, CFO Other Risk
1746 | GROUSE_CB_EOL | 3.5409 | 0.0029112 | 0.0029111 | 4.37e-07 | 0.00109% | EFF Risk, CFO Other Risk
1747 | WARDELL_PS0669_GS1117-4 | 0.76605 | 0.0028327 | 0.0028293 | 5.54e-05 | 0.00106% | EFF Risk, CFO Other Risk
1748 | STAGHORN_CB_RSR0233 | 0.37914 | 0.0028105 | 0.0028077 | 5.41e-06 | 0.00105% | EFF Risk, CFO Other Risk
1749 | PRIMROSE_RSR2716_RAR0961_RAR0960_ | 1.8674 | 0.0027923 | 0.0027891 | 1.68e-05 | 0.00105% | CFO Other Risk, EFF Risk
1750 | CARATAN_CB_RAR1414 | 2.2519 | 0.0027797 | 0.0027796 | 9.14e-07 | 0.00104% | EFF Risk, CFO Other Risk
1751 | WYLE_RCS4753_EOL | 0.36802 | 0.0027641 | 0.0027639 | 3.13e-06 | 0.00104% | CFO Other Risk, EFF Risk
1752 | TIMBER CANYON_RCS1535_RAR0255 | 2.7229 | 0.0027539 | 0.0027526 | 4.84e-06 | 0.00103% | CFO Other Risk, EFF Risk
1753 | GLASSCOCK_CB_RCS0624 | 6.7369 | 0.0027279 | 0.0027213 | 6.61e-05 | 0.00102% | EFF Risk, CFO Other Risk
1754 | GINGER_RCS0159_RAR2331_RAR0842_ | 1.9156 | 0.0027018 | 0.0027011 | 4.45e-06 | 0.00101% | CFO Other Risk, EFF Risk
1755 | MILPAS_CB_RCS9669 | 0.80606 | 0.0026854 | 0.0026811 | 2.44e-05 | 0.00101% | EFF Risk, CFO Other Risk
1756 | CARMELITA_BF00112_EOL | 0.87818 | 0.0026654 | 0.0026642 | 1.24e-05 | 0.001% | EFF Risk, CFO Other Risk
1757 | STEVENSON_RAR0288_EOL | 4.2452 | 0.0026635 | 0.0026634 | 3.53e-07 | 0.001% | EFF Risk, CFO Other Risk
1758 | RAYBURN_PS1245_EOL | 0.68322 | 0.0026503 | 0.0026488 | 6.31e-06 | 0.000995% | EFF Risk, CFO Other Risk
1759 | SEACLIFF_RAR0111_EOL | 0.90314 | 0.0026023 | 0.0026021 | 7.97e-06 | 0.000977% | EFF Risk, CFO Other Risk
1760 | BRADLEY_CB_EOL | 1.4757 | 0.0025952 | 0.0025946 | 1.13e-05 | 0.000974% | CFO Other Risk, EFF Risk
1761 | BASIL_PS1257_EOL | 0.6969 | 0.002586 | 0.002581 | 1.06e-05 | 0.00097% | EFF Risk, CFO Other Risk
1762 | REVERSE PEAK_RAR0112_EOL | 7.5175 | 0.0025832 | 0.0025777 | 1.45e-05 | 0.000969% | EFF Risk, CFO Other Risk
1763 | BOGART_RSR4674_EOL | 1.4656 | 0.0025824 | 0.002582 | 1.79e-05 | 0.000969% | EFF Risk, CFO Other Risk
1764 | KONA_RAR0324_EOL | 0.49136 | 0.0025552 | 0.0025489 | 7.89e-06 | 0.000959% | EFF Risk, CFO Other Risk
1765 | GREAT SALT_RAR7467_EOL | 1.9131 | 0.0025283 | 0.0025281 | 6.95e-06 | 0.000949% | EFF Risk, CFO Other Risk
1766 | NORTHPARK_CB_RCS2113 | 0.65576 | 0.0025211 | 0.0025206 | 8.83e-06 | 0.000946% | CFO Other Risk, EFF Risk
1767 | TRESTLE_RCS4652_EOL | 2.1016 | 0.0025154 | 0.0025128 | 1.61e-05 | 0.000944% | EFF Risk, CFO Other Risk
1768 | GOLDSMITH_GS1244-1_EOL | 0.37968 | 0.0025088 | 0.0025074 | 7.08e-06 | 0.000941% | EFF Risk, CFO Other Risk
1769 | KINNELOA_RCS0638_EOL [2] | 0.68749 | 0.0025086 | 0.0025068 | 4.53e-06 | 0.000941% | EFF Risk, CFO Other Risk
1770 | PANCHO_RAR3860_EOL | 0.75357 | 0.00249 | 0.0024879 | 3.16e-05 | 0.000934% | CFO Other Risk, EFF Risk
1771 | AGATE_RCS0263_RAR1297 | 0.96964 | 0.0024686 | 0.0024677 | 1.17e-05 | 0.000926% | EFF Risk, CFO Other Risk
1772 | ABACUS_GS0867-2_EOL | 0.74513 | 0.002438 | 0.0024373 | 2.9e-05 | 0.000915% | EFF Risk, CFO Other Risk
1773 | TEST_RSR0342_EOL | 4.3309 | 0.0024109 | 0.0024095 | 0.00013193 | 0.000905% | CFO Other Risk, EFF Risk
1774 | CLARINET_CB_RAR0627_RAR0299_ | 1.1892 | 0.0024079 | 0.0024055 | 5.35e-06 | 0.000904% | CFO Other Risk, EFF Risk
1775 | CALGROVE_RAR0071_RCS0072_RCS3916_ | 0.37886 | 0.0023911 | 0.0023906 | 1.6e-06 | 0.000897% | CFO Other Risk, EFF Risk
1776 | PRESLEY_CB_EOL | 0.26989 | 0.0023749 | 0.0023749 | 0 | 0.000891% | CFO Other Risk, EFF Risk
1777 | PATHE_RCS0926-2_EOL | 0.41962 | 0.0022917 | 0.0022917 | 2.36e-05 | 0.00086% | EFF Risk, CFO Other Risk
1778 | HOSPAT_GS1492-3_EOL | 0.62032 | 0.0022581 | 0.0022576 | 3.5e-06 | 0.000847% | CFO Other Risk, EFF Risk
1779 | DOMIC_PS0536_EOL | 0.87325 | 0.0022293 | 0.002229 | 1.9e-06 | 0.000837% | EFF Risk, CFO Other Risk
1780 | PLUTO_CB_EOL | 5.6089 | 0.0022069 | 0.0022049 | 2.31e-05 | 0.000828% | EFF Risk, CFO Other Risk
1781 | DUFFER_CB_PS0522 | 0.82362 | 0.0021524 | 0.0021497 | 1.68e-05 | 0.000808% | EFF Risk, CFO Other Risk
1782 | NAPA_CB_RCS0241_RAR7528_ | 0.59162 | 0.0021508 | 0.0021495 | 4.16e-06 | 0.000807% | EFF Risk, CFO Other Risk
1783 | CAMPROCK_CB_EOL | 4.0491 | 0.0021501 | 0.0021498 | 4.44e-07 | 0.000807% | EFF Risk, CFO Other Risk
1784 | GALENA_RSR6282_RSR0746 | 0.55894 | 0.0021357 | 0.0021347 | 4.39e-06 | 0.000801% | EFF Risk, CFO Other Risk
1785 | QUIXOTE_CB_EOL | 0.57521 | 0.0021345 | 0.0021345 | 2.1e-08 | 0.000801% | EFF Risk, CFO Other Risk
1786 | JARVIS_PS1456_EOL | 0.57796 | 0.0021092 | 0.0021091 | 1.45e-06 | 0.000792% | EFF Risk, CFO Other Risk
1787 | FIREBIRD_BF31047_EOL | 0.41991 | 0.0021027 | 0.0021027 | 3.1e-06 | 0.000789% | EFF Risk, CFO Other Risk
1788 | COBRA_RCS1448-2_EOL | 1.3218 | 0.0020769 | 0.0020739 | 5.69e-05 | 0.000779% | EFF Risk, CFO Other Risk
1789 | SEACLIFF_CB_RAR0111_RCS0751_ | 2.6999 | 0.0020531 | 0.0020512 | 2.5e-05 | 0.00077% | EFF Risk, CFO Other Risk
1790 | JUAREZ_CB_PS0544 | 1.0997 | 0.002041 | 0.0020401 | 1.8e-05 | 0.000766% | CFO Other Risk, EFF Risk
1791 | STEARNS_GS0632-2_EOL | 0.33998 | 0.0020026 | 0.0020014 | 5.7e-06 | 0.000751% | EFF Risk, CFO Other Risk
1792 | VERA CRUZ_CB_RAR7638 | 0.61001 | 0.0019871 | 0.001986 | 1.62e-06 | 0.000746% | CFO Other Risk, EFF Risk
1793 | CASE_RCS6411-3_EOL | 0.76455 | 0.001983 | 0.001983 | 1.77e-09 | 0.000744% | EFF Risk, CFO Other Risk
1794 | AVANTI_RAR1092_EOL | 0.25111 | 0.0019799 | 0.0019796 | 8.69e-06 | 0.000743% | EFF Risk, CFO Other Risk
1795 | REED_RAR0564_EOL | 0.42536 | 0.0019445 | 0.0019439 | 9e-06 | 0.00073% | CFO Other Risk, EFF Risk
1796 | VERDEMONT_RCS0823_RCS1101 | 0.90774 | 0.001944 | 0.001944 | 9.47e-08 | 0.00073% | EFF Risk, CFO Other Risk
1797 | DEVINE_GS0239-4_RCS0169 | 3.087 | 0.0019269 | 0.0019226 | 4.07e-05 | 0.000723% | EFF Risk, CFO Other Risk
1798 | HEAPS PEAK_CB_RCS0408 | 0.91038 | 0.0019268 | 0.0019268 | 2.26e-08 | 0.000723% | EFF Risk, CFO Other Risk
1799 | TIMBER CANYON_RAR0255_PS1081 | 2.6367 | 0.0019143 | 0.001914 | 3.78e-06 | 0.000718% | EFF Risk, CFO Other Risk
1800 | PRADO_CB_GS1204-1 | 0.29419 | 0.0018919 | 0.0018914 | 2.02e-05 | 0.00071% | CFO Other Risk, EFF Risk
1801 | BRAUN_GS9874-1_EOL | 2.4389 | 0.0018917 | 0.0018915 | 2.9e-05 | 0.00071% | EFF Risk, CFO Other Risk
1802 | SNOW VALLEY_RAR0025_EOL | 0.65635 | 0.0018816 | 0.001881 | 1.22e-05 | 0.000706% | EFF Risk, CFO Other Risk
1803 | SODA SPRINGS_RAR0532_RAR6579_RAR0145_ | 4.5017 | 0.0018668 | 0.001865 | 2.75e-05 | 0.000701% | EFF Risk, CFO Other Risk
1804 | PENSTOCK_PS0643_1687714E | 0.50249 | 0.0018315 | 0.0018311 | 1.35e-06 | 0.000687% | EFF Risk, CFO Other Risk
1805 | ZINC_CB_EOL | 3.0699 | 0.0018044 | 0.0018041 | 4.25e-05 | 0.000677% | EFF Risk, CFO Other Risk
1806 | BACHELOR_RCS0555_EOL | 3.248 | 0.00179 | 0.0017885 | 2.29e-05 | 0.000672% | EFF Risk, CFO Other Risk
1807 | DOLPHIN_CB_EOL | 1.1245 | 0.0017747 | 0.0017746 | 2e-07 | 0.000666% | EFF Risk, CFO Other Risk
1808 | BOMBAY_GS5532-3_PS0141 | 0.4453 | 0.0017658 | 0.0017658 | 9.42e-07 | 0.000663% | EFF Risk, CFO Other Risk
1809 | BELPAC_RAR5512_GS0404-2 | 0.39957 | 0.0017458 | 0.0017444 | 1.32e-05 | 0.000655% | EFF Risk, CFO Other Risk
1810 | DEACON_RAR2232_EOL | 0.61087 | 0.001699 | 0.0016982 | 3.08e-06 | 0.000638% | CFO Other Risk, EFF Risk
1811 | STEVENSON_CB_RAR0288_RAR0253_ | 3.7861 | 0.0016865 | 0.0016864 | 3.35e-07 | 0.000633% | EFF Risk, CFO Other Risk
1812 | BIG CREEK-PORTAL_RAR0006_RAR0918_RCS0002_ | 0.63185 | 0.0016739 | 0.0016739 | 1.57e-08 | 0.000628% | EFF Risk, CFO Other Risk
1813 | TWIN LAKES_GS8740-1_RCS0557 | 1.0486 | 0.0016553 | 0.0016489 | 5.83e-05 | 0.000621% | CFO Other Risk, EFF Risk
1814 | BOBSLED_CB_RCS0059 | 0.51672 | 0.001632 | 0.0016273 | 2.59e-05 | 0.000612% | EFF Risk, CFO Other Risk
1815 | ROS_PME6774-2_RSR7085 | 1.3505 | 0.0016186 | 0.0016181 | 6.59e-06 | 0.000607% | EFF Risk, CFO Other Risk
1816 | HURST_RAR0452_EOL | 1.3107 | 0.001616 | 0.0016139 | 1.08e-05 | 0.000606% | EFF Risk, CFO Other Risk
1817 | BRENNAN_PS0814_EOL | 0.54317 | 0.0016143 | 0.001614 | 4.75e-06 | 0.000606% | EFF Risk, CFO Other Risk
1818 | BONNIE_RAR1925_EOL | 0.26442 | 0.0015823 | 0.0015818 | 1.05e-06 | 0.000594% | EFF Risk, CFO Other Risk
1819 | CUPPLES_CB_RCS0061 | 1.3763 | 0.0015767 | 0.0015767 | 2.39e-07 | 0.000592% | CFO Other Risk, CFO VEG Risk
1820 | LA RICA_PS1362_EOL | 0.358 | 0.0015399 | 0.0015399 | 1.32e-07 | 0.000578% | EFF Risk, CFO Other Risk
1821 | PERIMETER_RCS0072_RAR0607_RAR0468_ | 4.9947 | 0.001533 | 0.0015288 | 3.3e-05 | 0.000575% | EFF Risk, CFO Other Risk
1822 | SPARKS_CB_EOL | 0.43377 | 0.0015173 | 0.0015165 | 4.58e-06 | 0.000569% | EFF Risk, CFO Other Risk
1823 | CUSHENBURY_CB_RCS0506 | 5.8965 | 0.0015025 | 0.0015024 | 4.9e-07 | 0.000564% | EFF Risk, CFO Other Risk
1824 | MILO_CB_PS9711 | 0.27884 | 0.0014929 | 0.0014927 | 7.72e-06 | 0.00056% | EFF Risk, CFO Other Risk
1825 | CRAB_RAR0051_RCS0432 | 0.59083 | 0.0014642 | 0.0014642 | 2.81e-08 | 0.000549% | CFO Other Risk, EFF Risk
1826 | LAWMAN_CB_RCS0595 | 0.43582 | 0.0014528 | 0.0014521 | 3.86e-06 | 0.000545% | CFO Other Risk, EFF Risk
1827 | VERDUGO_PS0663_EOL | 0.4614 | 0.0014322 | 0.0014297 | 4.79e-06 | 0.000537% | EFF Risk, CFO Other Risk
1828 | FIELDGATE_GS2200-4_EOL | 0.57027 | 0.0013983 | 0.001398 | 6.3e-06 | 0.000525% | CFO Other Risk, EFF Risk
1829 | CALORA_PS0848_GS3169-2 | 0.3848 | 0.0013895 | 0.0013895 | 2.56e-06 | 0.000521% | EFF Risk, CFO Other Risk
1830 | TRIUNFO_CB_RAR4570 | 0.32346 | 0.0013859 | 0.0013859 | 1.73e-06 | 0.00052% | CFO Other Risk, EFF Risk
1831 | ESCAMILLA_RCS1629_EOL | 0.59447 | 0.0013816 | 0.0013805 | 4.13e-05 | 0.000518% | CFO Other Risk, EFF Risk
1832 | CADENA_RCS4021_EOL | 0.80831 | 0.0013801 | 0.00138 | 3.15e-05 | 0.000518% | EFF Risk, CFO Other Risk
1833 | CANCUN_RCS5865-1_EOL | 0.36744 | 0.0013526 | 0.0013526 | 1.19e-06 | 0.000508% | CFO Other Risk, EFF Risk
1834 | MT. GIVENS_CB_EOL | 8.0814 | 0.0012992 | 0.0012991 | 4.91e-07 | 0.000488% | EFF Risk, CFO Other Risk
1835 | DOWELL_CB_EOL | 1.0037 | 0.0012992 | 0.0012991 | 4.78e-06 | 0.000488% | EFF Risk, CFO Other Risk
1836 | PRESTON_GS1925-2_EOL | 1.007 | 0.0012983 | 0.0012982 | 2.22e-06 | 0.000487% | CFO Other Risk, EFF Risk
1837 | BROOKINGS_CB_EOL | 0.29152 | 0.0012822 | 0.0012822 | 9.23e-09 | 0.000481% | EFF Risk, CFO Other Risk
1838 | MEDAL_RSR0178_EOL | 1.5254 | 0.0012791 | 0.0012788 | 2.83e-05 | 0.00048% | EFF Risk, CFO Other Risk
1839 | ESTABAN_RAR7446_EOL | 1.4276 | 0.0012684 | 0.001265 | 1.51e-05 | 0.000476% | EFF Risk, CFO Other Risk
1840 | KILKENNY_CB_RAR1258 | 0.45284 | 0.0012431 | 0.0012426 | 3.44e-06 | 0.000466% | CFO Other Risk, EFF Risk
1841 | HACIENDA_CB_EOL | 0.38786 | 0.0012396 | 0.0012286 | 0.00010121 | 0.000465% | CFO Other Risk, EFF Risk
1842 | RYE_RAR0654_EOL | 1.2814 | 0.0012271 | 0.0012267 | 2.35e-05 | 0.00046% | EFF Risk, CFO Other Risk
1843 | TERMINUS_RCS0450_EOL | 9.4197 | 0.0012111 | 0.0012108 | 5.17e-06 | 0.000454% | EFF Risk, CFO Other Risk
1844 | RHINEDOLLAR_CB_EOL | 1.5636 | 0.0012049 | 0.0012041 | 3.15e-06 | 0.000452% | EFF Risk, CFO Other Risk
1845 | BIG CREEK-PORTAL_CB_RCS0098_RAR0006_ | 0.54451 | 0.001204 | 0.001204 | 1.34e-08 | 0.000452% | EFF Risk, CFO Other Risk
1846 | OAKWOOD_CB_EOL | 4.194 | 0.0011959 | 0.0011938 | 1.84e-05 | 0.000449% | EFF Risk, CFO Other Risk
1847 | HOPE_RAR7107_EOL | 0.26121 | 0.0011447 | 0.0011425 | 3.05e-05 | 0.00043% | EFF Risk, CFO Other Risk
1848 | HUNTINGTON_CB_EOL | 1.1106 | 0.0011444 | 0.0011444 | 1.35e-06 | 0.000429% | EFF Risk, CFO Other Risk
1849 | EL MIRADOR_RAR2389_EOL | 0.77999 | 0.0011363 | 0.001136 | 4.96e-07 | 0.000426% | CFO Other Risk, EFF Risk
1850 | MALLET_RSR7780_EOL | 0.48134 | 0.0011188 | 0.001117 | 8.95e-06 | 0.00042% | CFO Other Risk, EFF Risk
1851 | SUTT_CB_RAR0939_RAR0818_ | 0.50315 | 0.0011162 | 0.0011143 | 5.99e-06 | 0.000419% | EFF Risk, CFO Other Risk
1852 | CARNEGIE_RAR5136_EOL | 1.0304 | 0.0011045 | 0.0010815 | 4.75e-05 | 0.000414% | EFF Risk, CFO Other Risk
1853 | RAMAC_RCS1820_EOL | 3.2571 | 0.0010725 | 0.0010711 | 1.46e-05 | 0.000402% | CFO Other Risk, EFF Risk
1854 | PERIMETER_RAR0607_EOL | 6.8422 | 0.0010714 | 0.0010694 | 3.49e-05 | 0.000402% | EFF Risk, CFO Other Risk
1855 | HURST_RCS0378_EOL | 1.06 | 0.0010677 | 0.0010587 | 1.89e-05 | 0.000401% | EFF Risk, CFO Other Risk
1856 | CHICO_PS0030_RAR0501 | 0.55076 | 0.0010563 | 0.0010558 | 1.02e-05 | 0.000396% | EFF Risk, CFO Other Risk
1857 | INTERIOR_CB_RSR0031_RAR0043_ | 1.8383 | 0.0010442 | 0.0010438 | 1.7e-05 | 0.000392% | CFO Other Risk, EFF Risk
1858 | GUNSITE_CB_EOL | 1.0045 | 0.0010421 | 0.0010421 | 3.4e-08 | 0.000391% | EFF Risk, CFO Other Risk
1859 | JUDSON_RCS0230_EOL | 0.40455 | 0.0010354 | 0.0010347 | 1.36e-05 | 0.000389% | EFF Risk, CFO Other Risk
1860 | ZIRCON_CB_GS5050-5 | 0.31242 | 0.0010339 | 0.001033 | 2.02e-05 | 0.000388% | EFF Risk, CFO Other Risk
1861 | RIDGEMOOR_GS0971-3_EOL | 0.53779 | 0.0010181 | 0.0010176 | 3.21e-05 | 0.000382% | EFF Risk, CFO Other Risk
1862 | LAUDA_CB_RAR7056_RAR1665_ | 0.30651 | 0.001007 | 0.001007 | 9.2e-09 | 0.000378% | EFF Risk, CFO Other Risk
1863 | JERRY_RCS7752_EOL | 0.62479 | 0.00099966 | 0.0009994 | 4.01e-06 | 0.000375% | CFO Other Risk, EFF Risk
1864 | ROI-TAN_PS1167_EOL | 0.32179 | 0.00095242 | 0.00095033 | 1.5e-05 | 0.000357% | CFO Other Risk, EFF Risk
1865 | DEACON_RCS0299_RAR2232 | 1.6766 | 0.00093537 | 0.00093496 | 5.91e-06 | 0.000351% | EFF Risk, CFO Other Risk
1866 | REEDER_RCS0381_EOL | 0.2933 | 0.00092002 | 0.00091933 | 1.61e-06 | 0.000345% | EFF Risk, CFO Other Risk
1867 | BAUXITE_CB_GS5567-3 | 2.837 | 0.00090904 | 0.00090743 | 8.71e-05 | 0.000341% | EFF Risk, CFO VEG Risk
1868 | SHOPPING_CB_EOL | 0.28515 | 0.00089085 | 0.00089007 | 9.01e-05 | 0.000334% | EFF Risk, CFO Other Risk
1869 | RAMAC_RAR0511_RCS1820 | 2.0511 | 0.0008678 | 0.00086565 | 1.05e-05 | 0.000326% | CFO Other Risk, EFF Risk
1870 | TWIN LAKES_GS1347-3_RCS1073-4 | 0.40642 | 0.00083476 | 0.00083226 | 2.26e-05 | 0.000313% | CFO Other Risk, EFF Risk
1871 | TURNPIKE_PS7122_EOL | 0.50556 | 0.00082396 | 0.00081919 | 8.95e-06 | 0.000309% | EFF Risk, CFO Other Risk
1872 | BIG CREEK-PORTAL_RCS0067_RCS0096 | 2.7575 | 0.00081275 | 0.00081274 | 6.92e-08 | 0.000305% | EFF Risk, CFO Other Risk
1873 | SNO CAT_CB_RCS0489 | 1.1257 | 0.00080075 | 0.00080075 | 7.31e-08 | 0.0003% | EFF Risk, CFO Other Risk
1874 | CITY OF BANNING #2_CB_EOL | 0.37327 | 0.00079379 | 0.00079379 | 0 | 0.000298% | EFF Risk, CFO Other Risk
1875 | STEARNS_RCS9871_GS0632-2 | 3.1931 | 0.00078821 | 0.00077674 | 5.3e-05 | 0.000296% | EFF Risk, CFO Other Risk
1876 | CENTAUR_RAR9554_EOL | 0.32833 | 0.0007864 | 0.00078623 | 4.8e-06 | 0.000295% | EFF Risk, CFO Other Risk
1877 | SOCRATES_PS0864_RAR0792 | 0.29656 | 0.00078407 | 0.00078325 | 3.14e-06 | 0.000294% | EFF Risk, CFO Other Risk
1878 | SEYMOUR_CB_RCS0430 | 4.2214 | 0.00073334 | 0.00073334 | 0 | 0.000275% | EFF Risk, CFO Other Risk
1879 | PYLE_RAR1284_EOL | 0.85968 | 0.00072826 | 0.00072742 | 2.11e-06 | 0.000273% | EFF Risk, CFO Other Risk
1880 | GRIDLOCK_RCS2395-4_EOL | 0.30506 | 0.00069355 | 0.00069335 | 1e-05 | 0.00026% | EFF Risk, CFO Other Risk
1881 | BLUEBERRY_CB_PS0723 | 0.33114 | 0.00066724 | 0.00066534 | 1.36e-05 | 0.00025% | EFF Risk, CFO Other Risk
1882 | SITZMARK_GS0085-3_EOL | 0.37766 | 0.00065768 | 0.00065567 | 7.52e-06 | 0.000247% | EFF Risk, CFO Other Risk
1883 | CATARACT_RCS3798_EOL | 0.48453 | 0.00065505 | 0.00065372 | 1.78e-06 | 0.000246% | EFF Risk, CFO Other Risk
1884 | GREAT SALT_CB_RAR7499_RAR7467_RAR8140 | 0.31289 | 0.00065097 | 0.00065054 | 7.8e-07 | 0.000244% | CFO Other Risk, EFF Risk
1885 | LESSER_PS0294_RCS0501 | 0.82785 | 0.00062096 | 0.00062074 | 2.43e-06 | 0.000233% | EFF Risk, CFO Other Risk
1886 | JUMBO_CB_EOL | 0.64717 | 0.00059767 | 0.00059767 | 1.81e-09 | 0.000224% | EFF Risk, CFO Other Risk
1887 | MUNICH_PME5653-1_PME5652-1 | 0.33662 | 0.00059505 | 0.00059502 | 0.00011398 | 0.000223% | EFF Risk, CFO Other Risk
1888 | STOCKER_CB_RAR0268 | 1.5066 | 0.00058731 | 0.00058673 | 2.85e-05 | 0.00022% | EFF Risk, CFO Other Risk
1889 | SHAMROCK_CB_EOL | 0.72414 | 0.00058604 | 0.00058442 | 6.33e-06 | 0.00022% | EFF Risk, CFO Other Risk
1890 | LAMBDA_RAR0149_EOL | 0.65931 | 0.00056939 | 0.00056892 | 6.01e-06 | 0.000214% | CFO Other Risk, EFF Risk
1891 | VASQUEZ_GS8000-2_GS3114-1 | 0.59674 | 0.00055917 | 0.00055238 | 8.33e-05 | 0.00021% | EFF Risk, CFO Other Risk
1892 | CHINA PEAK_RAR0242_EOL | 1.7688 | 0.00054718 | 0.00054718 | 2.57e-06 | 0.000205% | EFF Risk, CFO Other Risk
1893 | BIG CREEK-PORTAL_RAR0918_RCS0066 | 1.3402 | 0.00053596 | 0.00053595 | 3.22e-08 | 0.000201% | EFF Risk, CFO Other Risk
1894 | BRAND_CB_EOL | 1.5822 | 0.00053408 | 0.00052662 | 3.8e-05 | 0.0002% | EFF Risk, CFO Other Risk
1895 | MYRTLE_CB_EOL | 0.33693 | 0.00051136 | 0.00050902 | 3.25e-06 | 0.000192% | EFF Risk, CFO Other Risk
1896 | HANDY_RAR3591_EOL | 0.85335 | 0.0005019 | 0.0005 | 3.4e-06 | 0.000188% | CFO Other Risk, EFF Risk
1897 | CASPER_CB_EOL | 2.058 | 0.00050095 | 0.00050065 | 4.16e-07 | 0.000188% | EFF Risk, CFO Other Risk
1898 | WELCH_CB_RAR2295_PS3244_ | 1.2439 | 0.00049848 | 0.00049815 | 1.37e-06 | 0.000187% | CFO Other Risk, EFF Risk
1899 | FELDSPAR_RCS0494_GS4867-3 | 1.3739 | 0.0004812 | 0.0004812 | 2.01e-05 | 0.000181% | CFO Other Risk, EFF Risk
1900 | HESSION_BF50049_EOL | 3.573 | 0.00048035 | 0.00047851 | 7.6e-06 | 0.00018% | EFF Risk, CFO Other Risk
1901 | GRIDLOCK_BF13675_EOL | 0.40266 | 0.00047139 | 0.00047113 | 1.32e-05 | 0.000177% | EFF Risk, CFO Other Risk
1902 | GALENA_RSR0746_EOL | 0.51656 | 0.00043886 | 0.00043745 | 4.45e-06 | 0.000165% | CFO Other Risk, EFF Risk
1903 | OLIVER_CB_RCS8501_RAR7927_ | 0.31406 | 0.00042467 | 0.00042466 | 1.44e-08 | 0.000159% | EFF Risk, CFO Other Risk
1904 | DONLON_RAR0011_EOL | 0.31683 | 0.00041988 | 0.00041822 | 2.4e-06 | 0.000158% | EFF Risk, CFO Other Risk
1905 | BONNEVILLE_CB_RAR7500_RAR9025_ | 1.5147 | 0.00040455 | 0.00040382 | 2.32e-06 | 0.000152% | CFO Other Risk, EFF Risk
1906 | SAN NICHOLAS_RAR0753_RCS3642-1 | 0.40154 | 0.00040377 | 0.00039557 | 1.94e-05 | 0.000152% | EFF Risk, CFO Other Risk
1907 | PIEDRA_PS2137_EOL | 1.2828 | 0.0003812 | 0.00038109 | 3.01e-05 | 0.000143% | EFF Risk, CFO Other Risk
1908 | LIMA_CB_EOL | 1.202 | 0.00037131 | 0.00037044 | 5.41e-06 | 0.000139% | EFF Risk, CFO Other Risk
1909 | CONCORD_CB_EOL | 1.1508 | 0.00035613 | 0.00035454 | 1.03e-05 | 0.000134% | EFF Risk, CFO Other Risk
1910 | MONACHE_CB_RAR4242 | 0.63674 | 0.00034475 | 0.000344 | 1.16e-05 | 0.000129% | EFF Risk, CFO Other Risk
1911 | LILAC_CB_EOL | 2.9488 | 0.00034327 | 0.00034257 | 1.05e-05 | 0.000129% | EFF Risk, CFO Other Risk
1912 | GREENWELL_CB_EOL | 0.79943 | 0.00033953 | 0.00033953 | 8.03e-09 | 0.000127% | CFO Other Risk, EFF Risk
1913 | BIG CREEK-PORTAL_RCS0066_RCS0067 | 3.041 | 0.00032523 | 0.00032522 | 7.6e-08 | 0.000122% | EFF Risk, CFO Other Risk
1914 | FIELDGATE_CB_RCS4886-1 | 1.5661 | 0.00030258 | 0.000299 | 1.98e-05 | 0.000114% | CFO Other Risk, EFF Risk
1915 | ABRAHAM_GS4105-3_EOL | 0.46591 | 0.00029809 | 0.0002978 | 6.25e-05 | 0.000112% | EFF Risk, CFO Other Risk
1916 | BAZOOKA_CB_PME2111-3 | 0.35174 | 0.00028273 | 0.0002821 | 7.97e-07 | 0.000106% | EFF Risk, CFO Other Risk
1917 | LYTLE_PS2412_EOL | 0.73376 | 0.00028195 | 0.00028101 | 1.86e-06 | 0.000106% | EFF Risk, CFO Other Risk
1918 | ARTIST_RCS5643_EOL | 0.58915 | 0.00028042 | 0.00027848 | 2.92e-05 | 0.000105% | EFF Risk, CFO Other Risk
1919 | RAMAC_CB_RAR0511_RAR1867_ | 0.29054 | 0.00026398 | 0.00026175 | 3.45e-06 | 9.91e-05% | EFF Risk, CFO Other Risk
1920 | PRONGHORN_CB_RAR1079_RAR1263_ | 0.44018 | 0.00025118 | 0.0002421 | 1.06e-05 | 9.43e-05% | EFF Risk, CFO Other Risk
1921 | YOSEMITE_RCS0461_GS1788-3 | 1.3364 | 0.00024926 | 0.00024371 | 1.91e-05 | 9.35e-05% | EFF Risk, CFO Other Risk
1922 | TERMINUS_CB_RCS0450_RCS0172_ | 1.3942 | 0.00024822 | 0.00024809 | 8.74e-07 | 9.31e-05% | EFF Risk, CFO Other Risk
1923 | ROTEC_RCS1527_GS6582-1 | 0.75606 | 0.00022086 | 0.00022062 | 3.82e-06 | 8.29e-05% | EFF Risk, CFO Other Risk
1924 | PINZON_CB_RCS1049 | 0.99125 | 0.00022063 | 0.00021986 | 1.95e-05 | 8.28e-05% | EFF Risk, CFO Other Risk
1925 | SUTT_RAR0899_EOL | 0.35033 | 0.00020488 | 0.00020285 | 4.82e-06 | 7.69e-05% | CFO Other Risk, EFF Risk
1926 | ETHANAC_CB_PS0914 | 0.59973 | 0.00019658 | 0.00018937 | 1.29e-05 | 7.38e-05% | EFF Risk, CFO Other Risk
1927 | KWIS_RCS2205-4_EOL | 0.74427 | 0.00018571 | 0.0001849 | 1.42e-05 | 6.97e-05% | EFF Risk, CFO Other Risk
1928 | BIG CREEK-PORTAL_RCS0096_EOL | 2.4089 | 0.00018225 | 0.00018224 | 5.94e-08 | 6.84e-05% | EFF Risk, CFO Other Risk
1929 | SNO CAT_RCS0489_EOL | 0.70311 | 0.00017763 | 0.00017763 | 4.57e-08 | 6.67e-05% | EFF Risk, CFO Other Risk
1930 | CIENIGITAS_GS0819-3_EOL | 0.94299 | 0.00017334 | 0.00016756 | 1.77e-05 | 6.5e-05% | CFO Other Risk, EFF Risk
1931 | VERDUN_CB_EOL | 0.42917 | 0.00014811 | 0.00014788 | 5.21e-06 | 5.56e-05% | EFF Risk, CFO Other Risk
1932 | SESPE_CB_EOL | 0.51653 | 0.00014076 | 0.00014074 | 1.4e-07 | 5.28e-05% | EFF Risk, CFO Other Risk
1933 | LESSER_RCS0501_EOL | 0.95714 | 0.00013964 | 0.00013939 | 2.81e-06 | 5.24e-05% | EFF Risk, CFO Other Risk
1934 | TANDEM_CB_RCS1176_PS0121_ | 0.27403 | 0.00013934 | 0.0001392 | 2.26e-06 | 5.23e-05% | EFF Risk, CFO Other Risk
1935 | JOHNBOY_CB_GS1043-3 | 0.27332 | 0.00013201 | 0.00012765 | 3.74e-05 | 4.95e-05% | EFF Risk, Outage Risk
1936 | MANIFOLD_CB_EOL | 0.51959 | 0.0001137 | 0.0001137 | 0 | 4.27e-05% | EFF Risk, Outage Risk
1937 | VERDUGO_PS2294_RAR0900 | 4.493 | 0.00010831 | 0.00010403 | 2.6e-05 | 4.06e-05% | CFO Other Risk, EFF Risk
1938 | ROSEBUD_RAR0282_EOL | 1.6102 | 0.00010785 | 0.0001076 | 1.48e-06 | 4.05e-05% | EFF Risk, CFO Other Risk
1939 | VARGAS_RAR0828_RCS2937 | 0.72459 | 0.00010001 | 9.81e-05 | 8.12e-06 | 3.75e-05% | EFF Risk, CFO Other Risk
1940 | PLAYBOY_RAR4726_EOL | 0.26522 | 9.92e-05 | 9.84e-05 | 3.33e-05 | 3.72e-05% | EFF Risk, Outage Risk
1941 | PERIMETER_CB_RCS0072 | 0.53962 | 8.29e-05 | 8.13e-05 | 1.18e-05 | 3.11e-05% | CFO Other Risk, EFF Risk
1942 | GINGER_RAR0842_EOL | 2.7529 | 7.98e-05 | 7.92e-05 | 5.21e-06 | 2.99e-05% | EFF Risk, CFO Other Risk
1943 | PALOMA_CB_RCS0821-2 [2] | 0.29429 | 7.54e-05 | 7.47e-05 | 2.17e-06 | 2.83e-05% | CFO Other Risk, EFF Risk
1944 | CODONA_PS1196_EOL | 0.36972 | 6.79e-05 | 6.74e-05 | 2.37e-06 | 2.55e-05% | EFF Risk, CFO Other Risk
1945 | ANN_BF13356_EOL | 0.5287 | 6.33e-05 | 6.3e-05 | 9.09e-06 | 2.38e-05% | CFO Other Risk, EFF Risk
1946 | EASTER_RAR0250_RCS1196 | 0.71659 | 5.96e-05 | 5.94e-05 | 4.2e-06 | 2.24e-05% | EFF Risk, CFO Other Risk
1947 | NORTHRIDGE_CB_EOL | 0.33651 | 5.22e-05 | 5.22e-05 | 2.87e-06 | 1.96e-05% | EFF Risk, CFO Other Risk
1948 | OVERHILL_CB_EOL | 0.35913 | 5.22e-05 | 5.22e-05 | 1.34e-07 | 1.96e-05% | EFF Risk, CFO Other Risk
1949 | ACCENT_CB_GS5536-2 | 1.2756 | 5.15e-05 | 4.66e-05 | 2.3e-05 | 1.93e-05% | Outage Risk, EFF Risk
1950 | INTERN_RAR1181_EOL | 0.32248 | 4.59e-05 | 4.54e-05 | 2.3e-05 | 1.72e-05% | EFF Risk, Outage Risk
1951 | RAMAC_RCS1860_EOL | 0.29285 | 4.55e-05 | 4.52e-05 | 1.46e-06 | 1.71e-05% | CFO Other Risk, EFF Risk
1952 | TERRAZZO_CB_EOL | 0.29236 | 4.27e-05 | 4.27e-05 | 0 | 1.6e-05% | EFF Risk, CFO Other Risk
1953 | BRAUN_RCS2010-1_GS9874-1 | 0.26648 | 3.93e-05 | 3.92e-05 | 3.24e-06 | 1.47e-05% | EFF Risk, CFO Other Risk
1954 | ROXBURY_CB_EOL | 0.35792 | 3.12e-05 | 3.08e-05 | 3.9e-07 | 1.17e-05% | EFF Risk, CFO Other Risk
1955 | COLDWATER_CB_EOL | 1.2044 | 2.66e-05 | 2.63e-05 | 6.43e-06 | 9.99e-06% | EFF Risk, CFO Other Risk
1956 | READY_RCS0739_GS3095-4 | 0.27939 | 2.48e-05 | 2.25e-05 | 3.57e-06 | 9.3e-06% | EFF Risk, CFO Other Risk
1957 | SAVORY_RCS0094_EOL | 2.1464 | 2.08e-05 | 2.06e-05 | 8.39e-07 | 7.81e-06% | EFF Risk, CFO Other Risk
1958 | DILL_CB_GS2530-2 | 0.33847 | 1.76e-05 | 1.76e-05 | 1.44e-05 | 6.6e-06% | Outage Risk, EFF Risk
1959 | NAVEL_RCS0702_EOL | 0.25046 | 1.28e-05 | 1.28e-05 | 3.11e-06 | 4.79e-06% | CFO Other Risk, EFF Risk
1960 | HAVEN_RAR3880_EOL | 0.30452 | 1.14e-05 | 1.12e-05 | 1.48e-06 | 4.26e-06% | EFF Risk, CFO Other Risk
1961 | GREAT SALT_RAR8140_EOL | 1.9711 | 8.14e-06 | 7.75e-06 | 5.7e-06 | 3.05e-06% | Outage Risk, CFO Other Risk
1962 | MIDDLE ROAD_BF39701_EOL | 0.42866 | 1.72e-06 | 1.65e-06 | 4.47e-07 | 6.47e-07% | EFF Risk, Outage Risk
1963 | PALOMA_CB_RCS0821-2 | 0.29429 | 7.5428e-05 | 7.4692e-05 | 2.1738e-06 | 2.831e-05% | CFO Other Risk, EFF Risk
1964 | CODONA_PS1196_EOL | 0.36972 | 6.7897e-05 | 6.7402e-05 | 2.3719e-06 | 2.548e-05% | EFF Risk, CFO Other Risk
1965 | ANN_BF13356_EOL | 0.5287 | 6.3304e-05 | 6.3047e-05 | 9.0892e-06 | 2.376e-05% | CFO Other Risk, EFF Risk
1966 | EASTER_RAR0250_RCS1196 | 0.71659 | 5.9581e-05 | 5.9355e-05 | 4.2028e-06 | 2.236e-05% | EFF Risk, CFO Other Risk
1967 | NORTHRIDGE_CB_EOL | 0.33651 | 5.2246e-05 | 5.2246e-05 | 2.8737e-06 | 1.961e-05% | EFF Risk, CFO Other Risk
1968 | OVERHILL_CB_EOL | 0.35913 | 5.2246e-05 | 5.2246e-05 | 1.3381e-07 | 1.961e-05% | EFF Risk, CFO Other Risk
1969 | ACCENT_CB_GS5536-2 | 1.2756 | 5.1493e-05 | 4.6638e-05 | 2.3047e-05 | 1.932e-05% | Outage Risk, EFF Risk
1970 | INTERN_RAR1181_EOL | 0.32248 | 4.5871e-05 | 4.5415e-05 | 2.2959e-05 | 1.721e-05% | EFF Risk, Outage Risk
1971 | RAMAC_RCS1860_EOL | 0.29285 | 4.5455e-05 | 4.5187e-05 | 1.4619e-06 | 1.706e-05% | CFO Other Risk, EFF Risk
1972 | TERRAZZO_CB_EOL | 0.29236 | 4.2726e-05 | 4.2726e-05 | 0 | 1.603e-05% | EFF Risk, CFO Other Risk
1973 | BRAUN_RCS2010-1_GS9874-1 | 0.26648 | 3.9273e-05 | 3.9183e-05 | 3.2366e-06 | 1.474e-05% | EFF Risk, CFO Other Risk
1974 | ROXBURY_CB_EOL | 0.35792 | 3.1238e-05 | 3.0848e-05 | 3.9019e-07 | 1.172e-05% | EFF Risk, CFO Other Risk
1975 | COLDWATER_CB_EOL | 1.2044 | 2.6614e-05 | 2.6252e-05 | 6.4263e-06 | 9.987e-06% | EFF Risk, CFO Other Risk
1976 | READY_RCS0739_GS3095-4 | 0.27939 | 2.4788e-05 | 2.2512e-05 | 3.5689e-06 | 9.302e-06% | EFF Risk, CFO Other Risk
1977 | SAVORY_RCS0094_EOL | 2.1464 | 2.081e-05 | 2.0577e-05 | 8.3931e-07 | 7.809e-06% | EFF Risk, CFO Other Risk
1978 | DILL_CB_GS2530-2 | 0.33847 | 1.7582e-05 | 1.7582e-05 | 1.445e-05 | 6.598e-06% | Outage Risk, EFF Risk
1979 | NAVEL_RCS0702_EOL | 0.25046 | 1.2775e-05 | 1.2775e-05 | 3.11e-06 | 4.794e-06% | CFO Other Risk, EFF Risk
1980 | HAVEN_RAR3880_EOL | 0.30452 | 1.1356e-05 | 1.1206e-05 | 1.4779e-06 | 4.261e-06% | EFF Risk, CFO Other Risk
1981 | GREAT SALT_RAR8140_EOL | 1.9711 | 8.138e-06 | 7.7455e-06 | 5.7007e-06 | 3.054e-06% | Outage Risk, CFO Other Risk
1982 | MIDDLE ROAD_BF39701_EOL | 0.42866 | 1.7247e-06 | 1.6509e-06 | 4.4711e-07 | 6.472e-07% | EFF Risk, Outage Risk
[1] This circuit is located in the burn scar area of the Lidia Fire in January 2025.
[2] This circuit is located in the burn scar area of the Eaton Fire in January 2025.
[3] This circuit is located in the burn scar area of the Palisades Fire in January 2025.
[4] This circuit is located in the burn scar area of the Hughes Fire in January 2025.

## Table 6-2
Table 6-2: SCE Stakeholder Roles and Responsibilities in the Decision-Making Process
Stakeholder | Stakeholder Point of Contact | Electrical Corporation | Stakeholder Role | Engagement Methods | Activity | Level of Engagement for Activity
Point of Contact
SCE Executive Leadership | Director, Asset & System Intelligence | Director, Asset & System Intelligence | · Provides guidance and decision making on wildfire mitigation near and long-term planning | Weekly Internal Meetings | All | Internal
· Informed on wildfire mitigation execution status
· Informed and provides guidance on strategy/risk prioritization methodologies
Office of Energy Infrastructure Safety (OEIS or Energy Safety) | OEIS Deputy Director, Director of OEIS | Principal Manager, Regulatory Affairs & Compliance - State Regulatory Relations | · Defines WMP requirements | · Weekly meetings following submission of WMP | All | Local
|  |  | · Participates and provides guidance in working groups | · Biweekly participation in working groups
|  |  | · Reviews wildfire mitigation plan submissions and provides feedback, areas for continuous improvement, and issues approval or denial of plan | · Written comments
· Ad hoc meetings
California Public Utilities Commission (CPUC) | SED Director | Principal Manager, Regulatory Affairs & Compliance - State Regulatory Relations | · Provides guidance and review of CPUC-mandated risk analysis used to inform wildfire and PSPS mitigations; authorizes cost recovery for wildfire and PSPS mitigations in consideration of risk reduction, cost efficiency, affordability, and other factors. | · Ad hoc meetings | All | Local
· Comments, workshop, CPUC rulings and decisions
Local Governments (including city councils, county boards and tribal governments) | Various local representatives | Director, Local Public Affairs | · Provides feedback on implementation of SCE’s wildfire initiatives | Ad hoc meetings | All | Local; tribal
· Informed on SCE’s strategy as presented in WMP
Local Fire Agencies (includes Cal FIRE) | Various Southern California Fire Chiefs | Managing Director, Regulatory Relations | · Provides guidance on wildfire mitigations including Fire Suppression | Ad hoc meetings | All | Local
· Informed on SCE’s strategy as presented in WMP
Director, Business Resiliency
Cal OES | Assistant Director of Response Operations | Principal Manager, Regulatory Affairs & Compliance - State Regulatory Relations | · Provides statewide guidance on wildfire mitigations including PSPS | Ad hoc meetings | All | Local
· Participates on the board of the AFN Council
Access and Function Needs (AFN) Advisory Council | Various | VP Customer Engagement Division | Raises awareness of the needs of our AFN populations and to collaborate on initiatives that will advance communications, resources and support for AFN populations, all aimed at PSPS impact mitigation | Monthly meetings (or more frequent as necessary) | Wildfire Safety Community Meetings; Customer Research and Education; Critical Care Backup Battery; Portable Power Station and Generator Rebates | Local
Public Advocates Office and other stakeholders | Various | Various | Participates in Energy Safety-led working groups and provides input. | Pursuant to working group schedules | All | Local
Wildfire Safety Advisory Board | Board Members | Various | Advises OEIS on requirements for WMPs, holds workshops, provides comments on advisory opinions. | Comments, public meetings. | All | Local

## Table 6-3
Table 6-3: SCE Risk Impact of Activities
Activity | Activity Section # | Activity Effectiveness – Overall Risk | Activity Effectiveness – Wildfire Risk | Activity Effectiveness - Outage Program Risk | Risk Spend Efficiency Score - Overall Risk [1] | Risk Spend Efficiency Score - Wildfire Risk | Risk Spend Efficiency Score – Outage Program Risk | % HFTD Covered [2] | % HFTD/ HFRA Covered [3] | Expected % Risk Reduction [4] | Model(s) Used to Calculate Risk Impact
Covered Conductor (SH-1) | 8.2 | 60.45% | 60.45% | 61.86% | 1253.8543 | 1238.6383 | 15.216 | 4.716% | N/A | 0.4663% | POI; FireSight8
Undergrounding Overhead Conductor (SH-2) | 8.2 | 97.27% | 97.27% | 97.78% | 1468.1497 | 1464.5156 | 3.6341 | 2.784% | N/A | 1.911% | POI; FireSight8
REFCL GFN (SH-17) | 8.7 | 52.29% | 52.29% | 52.06% | 18919.7884 | 18918.0541 | 1.7343 | 4.863% | N/A | 1.425% | POI; FireSight8
REFCL GC (SH-18) | 8.7 | 48.11% | 48.11% | 47.89% | 22701.2356 | 22697.7313 | 3.5043 | 0.49% | N/A | 1.566% | POI; FireSight8
FR Wrap Expanded Deployment (SH-19) | 8.2 | 0.6951% | 0.6951% | N/A | 234.5144 | 234.5144 | N/A | 2.068% | N/A | 0.002673% | POI; FireSight8
Transmission Proactive Splice Shunting (SH-20) | 8.2 | 13.97% | 13.97% | N/A | 933.7922 | 933.7922 | N/A | 3.226% | N/A | 0.003723% | POI; FireSight8
Remote Controlled Automatic Reclosers Settings Update (SH-5) | 8.7 | 8.3% | 0% | 8.3% | 102.1654 | N/A | 102.1654 | 1.071% | N/A | 0.0007955% | POI; FireSight8
Long Span Initiative (SH-14) | 8.2 | 7.088% | 7.088% | 7.009% | 1288.8851 | 1288.8836 | 0.0015599 | 0.4815% | N/A | 0.02448% | POI; FireSight8
Distribution HFRI Inspections (Ground and Aerial) (IN-1.1) | 8.3 | 80.65% | 80.65% | 81.85% | 3454.1112 | 3454.0833 | 0.027861 | 100% | N/A | 4.977% | POI; FireSight8
Transmission HFRI Inspections (Ground and Aerial) (IN-1.2) | 8.3 | 77.1% | 77.1% | N/A | 113.082 | 113.082 | N/A | 100% | N/A | 0.03265% | POI; FireSight8
Distribution Infrared Scanning (IN-3) | 8.3 | 2.913% | 2.913% | 3.031% | 26.6443 | 26.6442 | 0.00014799 | 72.21% | N/A | 9.322e-05% | POI; FireSight8
Transmission Infrared and Corona Scanning (IN-4) | 8.3 | 16.95% | 16.95% | N/A | 8.643 | 8.643 | N/A | 50.42% | N/A | 6.213e-06% | POI; FireSight8
Generation HFRI Inspections (IN-5) | 8.3 | 80.65% | 80.65% | 81.85% | 129.6195 | 129.6194 | 0.00010279 | 0.1023% | N/A | 9.948e-05% | POI; FireSight8
HTMP (VM-1) | 9.2 | 60.48% | 60.48% | 60.48% | 742.3272 | 742.3271 | 8.4341e-05 | 100% | N/A | 0.1079% | POI; FireSight8
Dead & Dying Tree Removal (VM-4) | 9.2 | 51.27% | 51.27% | 51.27% | 1654.4393 | 1654.439 | 0.00030705 | 100% | N/A | 0.1605% | POI; FireSight8
Inspections for Vegetation Clearance from Distribution Lines (VM-7) | 9.2 | 97.09% | 97.09% | 97.09% | 214.0648 | 214.0644 | 0.00042345 | 100% | N/A | 5.041% | POI; FireSight8
Inspections for Vegetation Clearance from Transmission Lines (VM-8) | 9.2 | 95.91% | 95.91% | N/A | 356.201 | 356.201 | N/A | 100% | N/A | 1.126% | POI; FireSight8
Additional Structure Brushing (VM-2.1) | 9.4 | 32% | 32% | 32% | 16303.9752 | 16303.9633 | 0.011926 | 36.13% | N/A | 11.87% | POI; FireSight8
Compliance Structure Brushing (VM-2.2) | 9.4 | 32% | 32% | 32% | 42253.4653 | 42253.4437 | 0.021613 | 17.25% | N/A | 18.56% | POI; FireSight8
Early Fault Detection (EFD) (SA-11) | 10.3 | 9.956% | 9.956% | 9.908% | 5654.351 | 5653.9314 | 0.41967 | 6.416% | N/A | 0.244% | POI; FireSight8
[1] SCE has opted to use Risk Spend Efficiency Scores in lieu of Cost Benefit Ratios [2] SCE uses a 200-foot buffer extended from the HFTD to account for possible internal mapping discrepancies of assets as an additional margin for scoping enhanced wildfire mitigation activities. See D.19-05-038, Decision on Southern California Edison Company’s 2019 Wildfire Mitigation Plan Pursuant to Senate Bill 901, p. 7. [3] HFTD/HFRA meaning the combination of all HFTD and HFRA. At the time of this filing, all of SCE’s HFRA is now consistent with the CPUC HFTD maps. Please see % HFTD Covered. [4] This is the expected risk reduction from the first year of the Base plan to the last year of the Base plan based on implementation of the activity. [5] Please see Section 8.2 for more information about this activity.

## Table 6-4
Table 6-4: SCE Summary of Risk Reduction for Top-Risk Circuits [1]
Circuit, Segment, or Span ID | Initial Overall Utility Risk | 2026 Initiative Activities | 2026 Overall Utility Risk | 2027 Initiative Activities | 2027 Overall Utility Risk | 2028 Initiatives Activities | 2028 Overall Utility Risk
TUNGSTEN | 0.79861 | Covered Conductor, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Structure Brushing | 0.79861 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Structure Brushing | 0.79861 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.79861
PHEASANT | 3.1845 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 3.1845 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 3.1845 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 3.1845
LOUCKS | 1.3327 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.3327 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.3327 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.3327
PASCAL | 2.2653 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.2653 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.2653 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.2653
DAVENPORT | 12.8982 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 12.8982 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 12.8982 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 12.8982
CERRITO | 0.35024 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.35024 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.35024 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.35024
RAYBURN | 2.1132 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.1132 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.1132 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.1132
SHOVEL | 8.09 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 8.09 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 8.09 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 8.09
PELONA | 0.2989 | Transmission Proactive Splice Shunting, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.2989 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.2989 | Distribution HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.2989
GUFFY | 0.78051 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.78051 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.78051 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.77738
STORES | 4.2007 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.2007 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.2007 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.2007
PURCHASE | 0.56434 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.56434 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.56434 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.56434
ENERGY | 4.45 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.45 | Remote Controlled Automated Reclosers Settings Update, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.4498 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.4498
ARIEL | 0.049003 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.049003 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.049003 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.049003
BODKIN | 0.23424 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.23424 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.23424 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.23424
CASCADE | 0.9037 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.9037 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.9037 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.9037
IDA | 1.3463 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.3463 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.3463 | Distribution HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.3463
FINGAL | 4.5377 | REFCL Ground Fault Neutralizer, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.2845 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.2845 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.2845
POPPET FLATS | 4.0151 | REFCL Ground Fault Neutralizer, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.1825 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.1825 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.1825
STONEMAN | 3.1927 | Long Span Initiative, Distribution HFRI Inspections and Remediations, Distribution Infrared Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 3.1922 | Long Span Initiative, Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 3.1922 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 3.1922
PIONEERTOWN | 6.781 | Covered Conductor, REFCL Ground Fault Neutralizer, Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.9833 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.9833 | Distribution HFRI Inspections and Remediations, Structure Brushing | 2.9833
PICK [2] | 4.4893 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.4893 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.4893 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.4893
IRVINGTON | 0.025867 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.025867 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.02515 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.02515
PICONI | 1.9974 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.9974 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.9974 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.9974
SNOWCREEK | 0.17684 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.17684 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.17684 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.17684
NUTMEG | 0.77035 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.77035 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.77035 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.77035
SCHMIDT | 1.446 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.446 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.446 | Distribution HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.4417
SEAWOLF | 0.093915 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.093915 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.093915 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.093915
ARAPAHO | 1.4527 | Distribution HFRI Inspections and Remediations, Distribution Infrared Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.4527 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.4527 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.4527
MOAB | 0.048601 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.048601 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.048601 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.0486
LUISENO | 2.6053 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.6053 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.6053 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.6053
BALLOON | 0.35909 | Distribution HFRI Inspections and Remediations, Distribution Infrared Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.35909 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.35909 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.35909
BOUQUET | 2.0967 | Transmission Proactive Splice Shunting, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.0966 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.0966 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.0966
CALSPAR | 0.027505 | Long Span Initiative, Distribution HFRI Inspections and Remediations, Distribution Infrared Scanning, Structure Brushing | 0.02746 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.02746 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.02305
BIG ROCK | 1.1754 | Remote Controlled Automated Reclosers Settings Update, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Distribution Infrared Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.1754 | Long Span Initiative, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.1754 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 1.175
STAR ROCK | 0.19825 | Remote Controlled Automated Reclosers Settings Update, Distribution HFRI Inspections and Remediations, Structure Brushing | 0.19825 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.1982 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.1982
KELLER | 0.087326 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Structure Brushing | 0.087326 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.087326 | Distribution HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.087326
CORTESE | 0.17324 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.17324 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.17324 | Undergrounding Covered Conductor, Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.04319
BOOTLEGGER | 6.4508 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 6.4508 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 6.4508 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 6.4508
UTE | 0.080641 | Long Span Initiative, Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.07956 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.07956 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.07956
SOUTHRIDGE | 0.038649 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.03865 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.03569 | Covered Conductor, Distribution HFRI Inspections and Remediations, Structure Brushing | 0.03569
MOCKINGBIRD | 0.56335 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.56335 | Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.56335 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.56335
CORONITA | 0.035903 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.035903 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.035903 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.035903
ATENTO | 2.075 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.075 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.075 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 2.075
PAWNEE | 4.23 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.23 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.23 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 4.23
INYO LUMBER | 0.24229 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.24229 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.24229 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.24229
PARADISE | 1.1226 | Undergrounding Overhead Conductor, Long Span Initiative, Transmission Proactive Splice Shunting, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Distribution Infrared Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.28051 | Undergrounding Overhead Conductor, Long Span Initiative, Distribution HFRI Inspections and Remediations, Transmission HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.24101 | Distribution HFRI Inspections and Remediations, Transmission Infrared and Corona Scanning, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.24101
PERRIS | 0.25347 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.25347 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.25347 | Distribution HFRI Inspections and Remediations, Structure Brushing | 0.25347
RAMSGATE | 0.068345 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.068345 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.068345 | Distribution HFRI Inspections and Remediations, Hazard Tree Management Program, Structure Brushing, Dead and Dying Tree Removal | 0.068345
[1] Initial overall utility risk captures risk information as of 3/25/2025. 2026 Overall Risk, 2027 Overall Risk, and 2028 Overall Risk capture estimated risk information as of 12/31 of 2026, 2027, and 2028, respectively, based on forecasted deployment of mitigations presented in this WMP. [2] This circuit is located in the burn scar area of the Lidia Fire in January 2025.

## Table SCE 6-01
SCE 6-01: Mitigation Effectiveness
Tracking ID |  | Activity |  | Contact from | Contact from | Wire-to-wire | Equipment | Other | PSPS | PEDS
|  |  |  | Object - Veg. | Object - Other | contact | Failure [2]
SH-1 [1] |  | Covered Conductor | [6 empty] | Medium | Medium
SH-2 |  | Undergrounding Overhead Conductor | [6 empty] | High | High
SH-5 |  | Remote Controlled Automatic Reclosers |  | N/A | N/A | N/A | N/A | N/A | Low
N/A
SH-14 |  | Long Span Initiative (LSI) | [6 empty] | N/A | N/A
SH-17 |  | Rapid Earth Fault Current Limiters (REFCL) - Ground Fault Neutralizer | [6 empty] | N/A | N/A
SH-18 |  | REFCL - Grounding Conversion | [6 empty] | N/A | N/A
SH-19 [3] |  | Fire-resistant (FR) Wrap Expanded Deployment |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SH-20 |  | Transmission Proactive Splice Shunting |  | N/A | N/A | N/A |  | N/A | N/A | N/A
SA-11 |  | Early Fault Detection (EFD) | [6 empty] | N/A | N/A
IN-1.1 |  | Distribution High Fire Risk-Informed (HFRI) Inspections | [6 empty] | N/A | N/A
IN-1.2 |  | Transmission HFRI Inspections | [6 empty] | N/A | N/A
IN-3 |  | Distribution Infrared (IR) Scanning | [6 empty] | N/A | N/A
IN-4 |  | Transmission Infrared and Corona Scanning | [6 empty] | N/A | N/A
IN-5 |  | Generation HFRI Inspections | [6 empty] | N/A | N/A
VM-1 |  | Hazard Tree Management Program |  |  | N/A | N/A | N/A | N/A | N/A | N/A
VM-2 |  | Additional Structure Brushing |  | N/A | N/A | N/A |  | N/A | N/A | N/A
VM-2.2 |  | Compliance Structure Brushing |  |  | N/A | N/A |  | N/A
|  |  |  | N/A |  |  |  |  | N/A | N/A
VM-4 |  | Dead and Dying Tree Removal |  |  | N/A | N/A | N/A | N/A | N/A | N/A
VM-7 |  | Inspections for Vegetation Clearance from Distribution Lines | [6 empty] | N/A | N/A
VM-8 |  | Inspections for Vegetation Clearance from Transmission Lines |  |  | N/A | N/A | N/A | N/A | N/A | N/A
[1] Combines the effectiveness of covered conductor and FR Poles
[2] Equipment Failure is avg of Dist Conductor EFF Model
[3] The activity addresses "Reliability Risk" after fire incidents to restoration faster
| Legend |  | 0% effectiveness at driver level
0% to 25% effectiveness at driver level
25% to 50% effectiveness at driver level
50% to 75% effectiveness at driver level
75% to 100% effectiveness at driver level
|  | N/A | Driver is not applicable for mitigation

## Table SCE 6-02
Table SCE 6-02: Mitigation Effectiveness Sources
Tracking ID | Activity | Estimate Source
SH-1 | Covered Conductor | Formal analysis incorporating industry data with internal data
SH-2 | Undergrounding Overhead Conductor | Formal analysis incorporating industry data with internal data
SH-5 | Remote Controlled Automatic Reclosers Settings Update | Multiple SMEs
SH-14 | Long Span Initiative (LSI) | Multiple SMEs
SH-17 | Rapid Earth Fault Current Limiters (REFCL) - Ground Fault Neutralizer | Formal analysis incorporating industry data with internal data
SH-18 | REFCL - Grounding Conversion | Formal analysis incorporating industry data with internal data
SH-19 | Fire-resistant (FR) Wrap Expanded Deployment | Limited internal data
SH-20 | Transmission Proactive Splice Shunting | Multiple SMEs
SA-11 | Early Fault Detection (EFD) | Limited internal data
IN-1.1 | Distribution High Fire Risk-Informed (HFRI) Inspections | Internal data
IN- 1.2 | Transmission HFRI Inspections | Internal data
IN-3 | Distribution Infrared (IR) | Limited internal data
IN-4 | Transmission IR and Corona | Limited internal data
Scanning
IN-5 | Generation HFRI Inspections | Limited internal data
VM-1 | Hazard Tree Mitigation Program | Internal data
VM-2.1 | Additional Structure Brushing | Internal data
VM-2.2 | Compliance Structure Brushing | Internal data
VM-4 | Dead and Dying Tree Removal | Internal data
VM-7 | Inspections for Vegetation Clearance from Distribution Lines | Internal data
VM-8 | Inspections for Vegetation Clearance from Transmission Lines | Limited internal data

## Table SCE 6-03
Table SCE 6-03: Preferred Mitigation Portfolio per Risk Tranche
Risk Tranche | Preferred Mitigation Portfolio
Severe Risk Areas | TUG or REFCL/CC++, TVM/I++[1]
High Consequence Areas | CC++, TVM/I++
Other HFRA | VM/I++, TVM/I++
[1] SCE’s transmission lines also traverse SRAs, HCAs, and Other HFRAs.

## Table SCE 6-04
Table SCE 6-04: Activity Portfolios
Activity ID | Activity Name | TUG | REFCL/ CC++ | CC++ | VM/I++ | TVM/I++
IN-1.1 | Distribution HFRI Inspections | N/A | X | X | X | N/A
IN-1.2 | Transmission HFRI Inspections | N/A | N/A | N/A | N/A | X
IN-3 | Distribution IR | N/A | X | X | X | N/A
IN-4 | Transmission IR and Corona | N/A | N/A | N/A | N/A | X
IN-5 | Generation HFRI Inspections in HFRA | N/A | N/A | N/A | N/A | N/A
SA-11 | Early Fault Detection (EFD) | N/A | X | X | X | N/A
SH-1 | Covered Conductor | N/A | X | X | X | N/A
SH-14 | Long Span Initiative (LSI) | N/A | N/A | N/A | N/A | N/A
SH-17 | REFCL (Ground Fault Neutralizer) | N/A | X | N/A | N/A | N/A
SH-18 | REFCL ​(Grounding Conversion) | N/A | X | N/A | N/A | N/A
SH-19 | FR Wrap Expanded Deployment | N/A | X | X | N/A | N/A
SH-2 | Undergrounding Overhead Conductor | X | N/A | N/A | N/A | N/A
SH-20 | Transmission Proactive Splice Shunting | N/A | N/A | N/A | N/A | X
SH-5 | Remote Controlled Automatic Reclosers Settings Update | X | X | X | X | N/A
VM-1 | Hazard Tree Management Program | N/A | X | X | X | N/A
VM-14 | Expanded Clearances for Non-Energized Facilities | N/A | N/A | N/A | N/A | N/A
VM-2.1 | Additional Structure Brushing | N/A | X | X | X | X
VM-2.2 | Compliance Structure Brushing | N/A | X | X | X | X
VM-4 | Dead and Dying Tree Removal | N/A | X | X | X | N/A
VM-7 | Distribution VM Clearances | N/A | X | X | X | N/A
VM-8 | Transmission VM Clearances | N/A | N/A | N/A | N/A | X

## Table SCE 6-05
Table SCE 6-05: Efficacy of Activity Portfolios
Attribute | TUG | REFCL/CC++ | CC++ | VM/I++ | TVM/I++
Approximate Average lifetime cost/mile [1] | $2.9M-$4.5M+ [2] | $1.4M-$2.6M | $1.4M-$1.6M | $0.37M-$0.48M [3] | $0.16M-$0.21M
Deployment Speed [4] | 25-48+ months | 18-36+ months | 16-24+ months | Annual | Annual
Phase-to-phase incandescent particle ignition [5] mitigation | High | High | High | Low | Low
Phase-to-ground incandescent particle ignition [6] mitigation | High | High | High | Medium | Medium
Wire-down ignition mitigation | High | High | High | Low | Low
Equipment Failure mitigation | High | High | Medium | Medium | Medium
[1] Cost estimates associated with the VM/I++ and TVM/I++ portfolio are lifetime O&M costs and excludes Capital costs.
[2] Based on current analysis, SCE estimates that a small population of underground miles may fall below this range.
[3] Estimate of lifetime cost of the VM/I++ and TVM/I++ portfolio in Other HFRAs.
[4] Typical deployment timelines based on historical installations and projected costs. Actual timelines can vary further due to local conditions.
[5] Examples include conductor to conductor contact, balloon coming between two phase wires.
[6] Examples include tree to conductor contact, animal contact between phase wires and pole.

## Table SCE 6-06
Table SCE 6-06: Project Timelines for Select Wildfire Mitigations
Tracking ID | Mitigation | Initiate | Planning | Schedule | Execute | Total
SH-1 | Covered Conductor | 2-3 months | 6-9 months | 6-9 months | 2-3 months | 16 - 24 months
SH-2 | Undergrounding Overhead Conductor | 2-3 months | 9-15 months | 9-15 months | 5-15 months | 25 - 48 months
SH-5 | Remote Controlled Automatic Reclosers Settings Update | 1 - 3 months | 1-3 months | 1 - 2 months | 1 - 4 months | 4 - 12 months
SH-14 | Long Span Initiative (LSI) | 2 - 3 months | 1 - 9 months | 1 - 3 months | 1 - 6 months | 5 - 21 months
SH-17 | Rapid Earth Fault Current Limiters (REFCL) - Ground Fault Neutralizer | 2 - 3 months | 12 - 72 months | 4-9 months | 6 - 12 months | 24 - 96 months
SH-18 | REFCL - Grounding Conversion | 2 - 3 months | 4 - 18 months | 2 - 4 months | 2 - 4 months | 10 - 29 months
SH-19 | Fire-resistant (FR) Wrap Expanded Deployment | 2 -3 months | 3 - 4 months | 10 - 11 months | 10 - 11 months | 15 - 18 months
SH-20 | Transmission Proactive Splice Shunting | 1 - 2 months | 4 - 5 months | 2 - 3 months | 1 - 2 months | 8 - 12 months
SA-11 | Early Fault Detection (EFD) | 1 - 2 months | 3 - 6 months | 2 - 4 months | 3 - 6 months | 9 - 18 months